## 様式５_仕様書案 (hidden)
様式5
仕様書案
| 国名：ウクライナ国 | 案件名：ウクライナ国緊急復旧・復興プロジェクト向け機材（ヒートポンプ） | [8 empty] | 記入日：2023/11/15 Page： 1 /
| 機 材 名 | 仕 様 | メーカー名 | 数量 | JICSコメント／指摘根拠 | 指摘内容 | 見 積 書 価 格（円） |  |  |  | 備 考
採用価格
0 | 総則 |  |  |  | 総則の記載
仕様書の言語表記について、英・和（メーカー名等）表記が混在しているので、どちらかに統一することをお勧めします。
1 | WH-SXC16H9E8 (Indoor unit), WH-UX16E8(Outdoor unit) | Quantity：1 unit | パナソニック㈱ | 23 | 機材名は（調達機材総括表の機材名欄に記載されている）一般的な機材名称を記載（なお、銘柄名はWH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit)である点に注意） Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | WH-SXC16H9E8 (Indoor unit), WH-UX16E8(Outdoor unit)→Air Source Heat Pump Water Heater Quantity：1 unit→削除 パナソニック㈱→削除 23→削除 C14にC18の内容を移動 | 44391748 |  |  | 44391748
| A2W | Manufacturer：Panasonic or Equivalent |  |  | A2WがAir Source Heat Pump Water Heaterを指している場合、不要。削除。 Manufacturer：はメーカー名の項があるので不要。削除。 | A2W→削除 Manufacturer：Panasonic or Equivalent→削除 C15にC19の内容を移動
|  | Reference Model：WH-SXC16H9E8 (Indoor unit), WH-UX16E8(Outdoor unit) |  |  | 参考銘柄は仕様の後に記載する。削除 | 削除
|  | Country of Origin：Japan or EU |  |  | Country of Origin：は通常、定めないが適宜判断されてください。
General Description and function：Hot Water Heater
|  | Specifications Type：Split type air source heat pump water heater Heating Capacity：Not less than 16kW （Outdoor air condition: at-20℃） Coefficient of Performance： 2.49 at Air temp. -7°C and Water temp. 35 °C 1.86 at Air temp. -7°C and Water temp. 55 °C Supply hot water temperature Not less than 55℃（Temperature difference:5℃） Heating media Refrigerant Refrigerant Hydrofluorocarbons: ODP(ozone depletion potential) = 0 Electrical Characteristic Three Phase 380V 50Hz |  |  | スペース、コロンなどの整理 Heating Capacityの（Outdoor air condition: at-20℃）の記載意図不明。外気温に関係なく機材のHeating Capacityは16kWでは。 Heating media Refrigerant の意味が不明 | Specifications Type：Split type air source heat pump water heater Heating Capacity：Not less than 16kW Coefficient of Performance： 2.49 or surperior at Air temp. -7°C and Water temp. 35 °C 1.86 or surperior at Air temp. -7°C and Water temp. 55 °C Max. temperature of hot water supply：Not less than 55℃ Refrigerant：Hydrofluorocarbons ODP(ozone depletion potential)：0 Electrical Characteristic：Three Phase 380V 50Hz
|  | Accessory Hot water circulating pump（VFD Driven） PCB( Power Control Board) Base pan heater 3 way valve for DHW tanks Aquarea Smart Cloud 10 m extension cable Heat pumps group controller Modbus interface Sensors kit with cables（Outdoor ambient, Buffer tank, Zone water.） Outdoor base ground support Tray for condenser water compatible Outdoor elevation platform |  | 必要数量記載 | 確認対象外
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual（To be provided in Ukrainian or English） Parts catalog（To be provided in Ukrainian or English）
|  | Warranty Period 12 months after taking over |  |  | Warranty Periodは3アイテムに共通するため、総則への記載でも可。適宜判断願います。
|  | Others *QR code for Equipment Monitoring：After issuance of the Purchase Order, the Client will provide the Supplier a soft copy of the QR code sticker for monitoring system which is specified for each equipment. The Supplier shall print the stickers on 5 cm square by weather-resistant paper and paste it at least 3 locations on the left and right side of the equipment, the driver's seat, the vicinity of the control panel, etc., and it is easy for scanning and difficult to stain. The Supplier shall also provide at least 2 spares of each sticker with the instructions. *ODA Sticker "Complied. Refer to Clause 16 of Annex-2 Delivery Requirements." *Declaration of Conformity (DoC）in Ukraine：Required *Documentation support for registration of the number plate for driving on public roads：To be provided | 赤字：梱包条件書に転記 黒字：記載を残す 青字：削除 以下２，３ｱｲﾃﾑ共通 |  | 確認対象外
[5 empty] | 参考銘柄は仕様の後に記載する。 メーカー名を記載 数量を記載 | Reference Model：WH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit) パナソニック㈱ 23
|  | 稼働監視システム for Air source heat pump water heater | パナソニック㈱ | 5 | アイテム番号を記載（アイテム1の枝番） 機材名を記載 メーカー名は削除 数量を削除 仕様の記載 | 1-2 外機連結システム for Air source heat pump water heater パナソニック㈱→削除 5→削除 数値での仕様の記載が難しい場合、システムの用途、機能など最低限の仕様を提示する必要がある。 | 1661130 |  |  | 1661130
[5 empty] | 参考銘柄を記載 メーカー名を記載 数量を記載 | Reference Model：Cascade Manager PAW-A2W-CMH-2 パナソニック㈱ 5
2 | FY-15CSD1 | Quantity：1 unit | パナソニック㈱ | 10 | 機材名は一般的な機材名称を記載（なお、銘柄名はFV-15CSD1である点に注意） Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | FY-15CSD1→Air Purification Unit Quantity：1 unit→削除 パナソニック㈱→削除 10→削除 | 316410 |  |  | 316410
| APU | Manufacturer：Panasonic or Equivalent |  |  | APUがAir Purification Unitを指している場合、不要。削除。 Manufacturer：はメーカー名の項があるので不要。削除。 | APU→削除 Manufacturer：Panasonic or Equivalent→削除
|  | Reference Model：FY-15CSD1 |  |  | 参考銘柄は仕様の後に記載する。削除 | 削除
|  | Country of Origin：Japan or EU |  |  | Country of Origin：は通常、定めないが適宜判断されてください。
General Description and function：Air purification unit
|  | Specifications Type Ionization Air Purification Unit with Humidifying function Installation Ceiling mounted Air flow rate Not less than 15m3/hour Noise level Less than 28 dB(A) at 1.0 meter remote Electrical Characteristic Single phase 220V 50Hz |  |  | スペース、コロンなどの整理 | Specifications Type：Ionization Air Purification Unit with Humidifying function Installation：Ceiling mounted Air flow rate：Not less than 15m3/hour Noise level：Less than 28 dB(A) at 1.0 meter remote Electrical Characteristic：Single phase 220V 50Hz
|  | Accessory：None |  |  | Accessory：が無い場合は項目自体、記載しない。 | 削除
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual：To be provided in Ukrainian or English
|  | Warranty Period：12 months after taking over |  |  | Warranty Periodは3アイテムに共通するため、総則への記載でも可。適宜判断願います。
|  | Others： *QR code for Equipment Monitoring：After issuance of the Purchase Order, the Client will provide the Supplier a soft copy of the QR code sticker for monitoring system which is specified for each equipment. The Supplier shall print the stickers on 5 cm square by weather-resistant paper and paste it at least 3 locations on the left and right side of the equipment, the driver's seat, the vicinity of the control panel, etc., and it is easy for scanning and difficult to stain. The Supplier shall also provide at least 2 spares of each sticker with the instructions. *ODA Sticker："Complied. Refer to Clause 16 of Annex-2 Delivery Requirements." *Declaration of Conformity (DoC）in Ukraine：Required *Documentation support for registration of the number plate for driving on public roads：To be provided |  |  | 確認対象外
[5 empty] | 参考銘柄は仕様の後に記載する。（32行目参照） メーカー名を記載 数量を記載 | Reference Model：FV-15CSD1 パナソニック㈱ 10
3 | CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) | Quantity：1 unit | パナソニック㈱ | 5 | 機材名は一般的な機材名称を記載 Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit)→Split type Heat Pump Air Conditioner Quantity：1 unit→削除 パナソニック㈱→削除 5→削除 | 1344725 |  |  | 1344725
| A2A | Manufacturer：Panasonic or Equivalent |  |  | A2AがSplit type Heat Pump Air Conditionerを指している場合、不要。削除。 Manufacturer：はメーカー名の項があるので不要。削除。 | 削除
|  | Reference Model：CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) |  |  | 参考銘柄は仕様の後に記載する。削除 | 削除
|  | Country of Origin：Japan or EU |  |  | Country of Origin：は通常、定めないが適宜判断されてください。
General Description and function：Air Conditioners
|  | Specifications： Type Split type air -air heat pump air conditioner Indoor Unit Type Wall mounted Heating Capacity Not less than 4.3kW （Outdoor air condition: at－20℃） Outdoor Unit Coefficient of Performance Not less than 2.56 at Air temp. -7°C Refrigerant Hydrofluorocarbons: ODP(ozone depletion potential) = 0 Electrical Characteristic Single phase 220V 50Hz |  |  | スペース、コロンなどの整理 Heating Capacityの（Outdoor air condition: at-20℃）の記載意図不明。外気温に関係なく機材のHeating Capacityは4.3kWでは。 | Specifications： Type：Split type air -air heat pump air conditioner Indoor Unit Type：Wall mounted Heating Capacity：Not less than 4.3kW Outdoor Unit Coefficient of Performance：Not less than 2.56 at Air temp. -7°C Refrigerant：Hydrofluorocarbons ODP(ozone depletion potential)：0 Electrical Characteristic：Single phase 220V 50Hz
|  | Accessory： Remote controller：Built-in Wi-Fi interface Refrigerant pipe：Liquid and gas piping with insulation Outdoor base ground support Outdoor elevation platform |  |  | 確認対象外
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual：To be provided in Ukrainian or English
|  | Warranty Period：12 months after taking over |  |  | Warranty Periodは3アイテムに共通するため、総則への記載でも可。適宜判断願います。
|  | Others： *QR code for Equipment Monitoring：After issuance of the Purchase Order, JICS will provide the Supplier a soft copy of the QR code sticker for monitoring system which is specified for each equipment. The Supplier shall print the stickers on 5 cm square by weather-resistant paper and paste it at least 3 locations on the left and right side of the equipment, the driver's seat, the vicinity of the control panel, etc., and it is easy for scanning and difficult to stain. The Supplier shall also provide at least 2 spares of each sticker with the instructions. *ODA Sticker："Complied. Refer to Clause 16 of Annex-2 Delivery Requirements." *Declaration of Conformity (DoC）in Ukraine：Required *Documentation support for registration of the number plate for driving on public roads：To be provided |  |  | 確認対象外
[5 empty] | 参考銘柄は仕様の後に記載する。（44行目参照） メーカー名を記載 数量を記載 | Reference Model：CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) パナソニック㈱ 5
0
0
合 計 | [6 empty] | 47714013 | 0 | 0 | 47714013
切りとり線

## 様式５_仕様書案 (2) (hidden)
様式5
仕様書案
| 国名：ウクライナ国 | 案件名：ウクライナ国緊急復旧・復興プロジェクト向け機材（ヒートポンプ） | [8 empty] | 記入日：2023/11/15 Page： 1 /
| 機 材 名 | 仕 様 | メーカー名 | 数量 | JICSコメント／指摘根拠 | 指摘内容 | 見 積 書 価 格（円） |  |  |  | 備 考 | 松原コメント
採用価格
0 | 総則 | （総則） |  |  | 総則の記載
|  | 1. 中古品は認めない。 |  |  | 仕様書の言語表記について、英・和（メーカー名等）表記が混在しているので、どちらかに統一することをお勧めします。
2. 仕様欄において、「程度」と付記された数値は、その数値を中
心値として、±10％以内の範囲を認める。
3. 電源を必要とする機材の電源仕様は、単相AC230V、50Hz、
または内蔵ﾊﾞｯﾃﾘｰを使用するものとする。但し、各機材の
仕様欄に電源仕様の記載がある場合にはそれに従うこと。
4. 電源を必要とする機材については、仕様書に記載の有無にかか
わらず、機材を正常に作動させるために必要とされる資機材
（電源ｹｰﾌﾞﾙ、変換ﾌﾟﾗｸﾞ、電圧変換器など）は、当該機材に
含め、契約締結時に内訳明細書に記載すること。
5. 単相の電源ﾌﾟﾗｸﾞﾀｲﾌﾟは、各機材の仕様欄に記載のとおりCﾀｲﾌﾟ
であること。機材の電源ﾌﾟﾗｸﾞが指定のﾀｲﾌﾟに対応
できない場合は、変換ﾌﾟﾗｸﾞの使用を認める。
6. 電源を必要とする機材は、当該機材が現地 電源電圧に対応
できない場合、当該機材が正常に作動するために必要な定格容量を
満たすﾄﾗﾝｽを含めること。ﾄﾗﾝｽを含める場合、
契約内訳書作成時に個々のﾄﾗﾝｽのﾒｰｶｰ名、型式、型番、および
仕様（入出力電圧、定格容量など）を明記すること。
7. ﾒｰｶｰ設定の標準付属品は、仕様欄に記載がなくとも当該機材の
付属品として含め、契約内訳書作成時に個々のﾒｰｶｰ名、型式、
型番、および数量などを明記すること。
8. 機材を設置し、同機材が正常に作動するために必要な資機材
(据え付け部材、電源ｹｰﾌﾞﾙ、ﾄﾗﾝｽなど)は、仕様欄に記
載がなくとも当該機材に含めること。
9. 本件は納入前立会検査と技師派遣業務完了時検査を一括で
行い、費用の支払いは検査が完了した時点で請求可能とする。
10. 受注者は、仕向地における立会検査の際、ｵﾝﾗｲﾝで立ち会う
こと。
11. 機材引渡し後1年間の保証を付すること。
12. Declaration of Conformity (DoC）取得済みの機材または、
納入前に取得し、納入すること。
1 | WH-SXC16H9E8 (Indoor unit), WH-UX16E8(Outdoor unit) Air Source Heat Pump Water Heater | Quantity：1 unit General Description and function：Hot Water Heater | パナソニック㈱ | 23 | 機材名は（調達機材総括表の機材名欄に記載されている）一般的な機材名称を記載（なお、銘柄名はWH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit)である点に注意） Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | WH-SXC16H9E8 (Indoor unit), WH-UX16E8(Outdoor unit)→Air Source Heat Pump Water Heater Quantity：1 unit→削除 パナソニック㈱→削除 23→削除 C14にC18の内容を移動 | 44391748 |  |  | 44391748
| A2W | Manufacturer：Panasonic or Equivalent Specifications Type：Split type air source heat pump water heater Heating Capacity：Not less than 16kW Coefficient of Performance： 2.49 or surperior at Air temp. -7°C and Water temp. 35 °C 1.86 or surperior at Air temp. -7°C and Water temp. 55 °C Max. temperature of hot water supply：Not less than 55℃ Refrigerant：Hydrofluorocarbons ODP(ozone depletion potential)：0 Electrical Characteristic：Three Phase 380V 50Hz |  |  | A2WがAir Source Heat Pump Water Heaterを指している場合、不要。削除。 Manufacturer：はメーカー名の項があるので不要。削除。 | A2W→削除 Manufacturer：Panasonic or Equivalent→削除 C15にC19の内容を移動
|  | Reference Model：WH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit) |  |  | 参考銘柄は仕様の後に記載する。削除 | 削除
|  | Country of Origin：Japan or EU |  |  | Country of Origin：は通常、定めないが適宜判断されてください。 | [6 empty] | 納期でかなり限られますので、あえて制限せず、代替銘柄の提案を受け入れるしせを出したいです。
General Description and function：Hot Water Heater
|  | Specifications Type：Split type air source heat pump water heater Heating Capacity：Not less than 16kW （Outdoor air condition: at-20℃） Coefficient of Performance： 2.49 at Air temp. -7°C and Water temp. 35 °C 1.86 at Air temp. -7°C and Water temp. 55 °C Supply hot water temperature Not less than 55℃（Temperature difference:5℃） Heating media Refrigerant Refrigerant Hydrofluorocarbons: ODP(ozone depletion potential) = 0 Electrical Characteristic Three Phase 380V 50Hz |  |  | スペース、コロンなどの整理 Heating Capacityの（Outdoor air condition: at-20℃）の記載意図不明。外気温に関係なく機材のHeating Capacityは16kWでは。 Heating media Refrigerant の意味が不明 | Specifications Type：Split type air source heat pump water heater Heating Capacity：Not less than 16kW Coefficient of Performance： 2.49 or surperior at Air temp. -7°C and Water temp. 35 °C 1.86 or surperior at Air temp. -7°C and Water temp. 55 °C Max. temperature of hot water supply：Not less than 55℃ Refrigerant：Hydrofluorocarbons ODP(ozone depletion potential)：0 Electrical Characteristic：Three Phase 380V 50Hz
|  | Accessory Hot water circulating pump（VFD Driven） PCB( Power Control Board) Base pan heater 3 way valve for DHW tanks Aquarea Smart Cloud 10 m extension cable Heat pumps group controller Modbus interface Sensors kit with cables（Outdoor ambient, Buffer tank, Zone water.） Outdoor base ground support Tray for condenser water compatible Outdoor elevation platform 外機連結システム（５台） 概要 Reference Model：Cascade Manager PAW-A2W-CMH-2 | パナソニック㈱ | 必要数量記載 | 確認対象外
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual（To be provided in Ukrainian or English） Parts catalog（To be provided in Ukrainian or English）
|  | Warranty Period 12 months after taking over |  |  | Warranty Periodは3アイテムに共通するため、総則への記載でも可。適宜判断願います。 | [6 empty] | 総則へ追記
|  | Others *QR code for Equipment Monitoring：After issuance of the Purchase Order, the Client will provide the Supplier a soft copy of the QR code sticker for monitoring system which is specified for each equipment. The Supplier shall print the stickers on 5 cm square by weather-resistant paper and paste it at least 3 locations on the left and right side of the equipment, the driver's seat, the vicinity of the control panel, etc., and it is easy for scanning and difficult to stain. The Supplier shall also provide at least 2 spares of each sticker with the instructions. *ODA Sticker "Complied. Refer to Clause 16 of Annex-2 Delivery Requirements." *Declaration of Conformity (DoC）in Ukraine：Required *Documentation support for registration of the number plate for driving on public roads：To be provided | 赤字：梱包条件書に転記 黒字：記載を残す 青字：削除 以下２，３ｱｲﾃﾑ共通 |  | 確認対象外
|  | Reference Model：WH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit) | パナソニック㈱ | 23 | 参考銘柄は仕様の後に記載する。 メーカー名を記載 数量を記載 | Reference Model：WH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit) パナソニック㈱ 23
|  | 稼働監視システム for Air source heat pump water heater | パナソニック㈱ | 5 | アイテム番号を記載（アイテム1の枝番） 機材名を記載 メーカー名は削除 数量を削除 仕様の記載 | 1-2 外機連結システム for Air source heat pump water heater パナソニック㈱→削除 5→削除 数値での仕様の記載が難しい場合、システムの用途、機能など最低限の仕様を提示する必要がある。 | 1661130 |  |  | 1661130
[5 empty] | 参考銘柄を記載 メーカー名を記載 数量を記載 | Reference Model：Cascade Manager PAW-A2W-CMH-2 パナソニック㈱ 5 | [5 empty] | C20に付属品として追記
2 | FY-15CSD1 Air Purification Unit | Quantity：1 unit General Description and function：Air purification unit | パナソニック㈱ | 10 | 機材名は一般的な機材名称を記載（なお、銘柄名はFV-15CSD1である点に注意） Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | FY-15CSD1→Air Purification Unit Quantity：1 unit→削除 パナソニック㈱→削除 10→削除 | 316410 |  |  | 316410
| APU | Manufacturer：Panasonic or Equivalent |  |  | APUがAir Purification Unitを指している場合、不要。削除。 Manufacturer：はメーカー名の項があるので不要。削除。 | APU→削除 Manufacturer：Panasonic or Equivalent→削除
|  | Reference Model：FY-15CSD1 |  |  | 参考銘柄は仕様の後に記載する。削除 | 削除
|  | Country of Origin：Japan or EU |  |  | Country of Origin：は通常、定めないが適宜判断されてください。 | [6 empty] | アイテムと同じ理由で削除
General Description and function：Air purification unit
|  | Specifications Type：Ionization Air Purification Unit with Humidifying function Installation：Ceiling mounted Air flow rate：Not less than 15m3/hour Noise level：Less than 28 dB(A) at 1.0 meter remote Electrical Characteristic：Single phase 220V 50Hz |  |  | スペース、コロンなどの整理 | Specifications Type：Ionization Air Purification Unit with Humidifying function Installation：Ceiling mounted Air flow rate：Not less than 15m3/hour Noise level：Less than 28 dB(A) at 1.0 meter remote Electrical Characteristic：Single phase 220V 50Hz
|  | Accessory：None |  |  | Accessory：が無い場合は項目自体、記載しない。 | 削除
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual：To be provided in Ukrainian or English
|  | Warranty Period：12 months after taking over |  |  | Warranty Periodは3アイテムに共通するため、総則への記載でも可。適宜判断願います。 | [6 empty] | 総則へ追記
|  | Others： *QR code for Equipment Monitoring：After issuance of the Purchase Order, the Client will provide the Supplier a soft copy of the QR code sticker for monitoring system which is specified for each equipment. The Supplier shall print the stickers on 5 cm square by weather-resistant paper and paste it at least 3 locations on the left and right side of the equipment, the driver's seat, the vicinity of the control panel, etc., and it is easy for scanning and difficult to stain. The Supplier shall also provide at least 2 spares of each sticker with the instructions. *ODA Sticker："Complied. Refer to Clause 16 of Annex-2 Delivery Requirements." *Declaration of Conformity (DoC）in Ukraine：Required *Documentation support for registration of the number plate for driving on public roads：To be provided |  |  | 確認対象外
|  | Reference Model：FV-15CSD1 | パナソニック㈱ | 10 | 参考銘柄は仕様の後に記載する。（32行目参照） メーカー名を記載 数量を記載 | Reference Model：FV-15CSD1 パナソニック㈱ 10
3 | CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) Split type Heat Pump Air Conditioner | Quantity：1 unit General Description and function：Air Conditioners | パナソニック㈱ | 5 | 機材名は一般的な機材名称を記載 Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit)→Split type Heat Pump Air Conditioner Quantity：1 unit→削除 パナソニック㈱→削除 5→削除 | 1344725 |  |  | 1344725
| A2A | Manufacturer：Panasonic or Equivalent |  |  | A2AがSplit type Heat Pump Air Conditionerを指している場合、不要。削除。 Manufacturer：はメーカー名の項があるので不要。削除。 | 削除
|  | Reference Model：CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) |  |  | 参考銘柄は仕様の後に記載する。削除 | 削除
|  | Country of Origin：Japan or EU |  |  | Country of Origin：は通常、定めないが適宜判断されてください。 | [6 empty] | アイテム１と同じ理由で削除
General Description and function：Air Conditioners
|  | Specifications： Type Split type air -air heat pump air conditioner Indoor Unit Type Wall mounted Heating Capacity Not less than 4.3kW （Outdoor air condition: at－20℃） Outdoor Unit Coefficient of Performance Not less than 2.56 at Air temp. -7°C Refrigerant Hydrofluorocarbons: ODP(ozone depletion potential) = 0 Electrical Characteristic Single phase 220V 50Hz |  |  | スペース、コロンなどの整理 Heating Capacityの（Outdoor air condition: at-20℃）の記載意図不明。外気温に関係なく機材のHeating Capacityは4.3kWでは。 | Specifications： Type：Split type air -air heat pump air conditioner Indoor Unit Type：Wall mounted Heating Capacity：Not less than 4.3kW Outdoor Unit Coefficient of Performance：Not less than 2.56 at Air temp. -7°C Refrigerant：Hydrofluorocarbons ODP(ozone depletion potential)：0 Electrical Characteristic：Single phase 220V 50Hz
|  | Accessory： Remote controller：Built-in Wi-Fi interface Refrigerant pipe：Liquid and gas piping with insulation Outdoor base ground support Outdoor elevation platform |  |  | 確認対象外
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual：To be provided in Ukrainian or English
|  | Warranty Period：12 months after taking over |  |  | Warranty Periodは3アイテムに共通するため、総則への記載でも可。適宜判断願います。 | [6 empty] | 総則へ追記
|  | Others： *QR code for Equipment Monitoring：After issuance of the Purchase Order, JICS will provide the Supplier a soft copy of the QR code sticker for monitoring system which is specified for each equipment. The Supplier shall print the stickers on 5 cm square by weather-resistant paper and paste it at least 3 locations on the left and right side of the equipment, the driver's seat, the vicinity of the control panel, etc., and it is easy for scanning and difficult to stain. The Supplier shall also provide at least 2 spares of each sticker with the instructions. *ODA Sticker："Complied. Refer to Clause 16 of Annex-2 Delivery Requirements." *Declaration of Conformity (DoC）in Ukraine：Required *Documentation support for registration of the number plate for driving on public roads：To be provided |  |  | 確認対象外
|  | Reference Model：CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) | パナソニック㈱ | 5 | 参考銘柄は仕様の後に記載する。（44行目参照） メーカー名を記載 数量を記載 | Reference Model：CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) パナソニック㈱ 5
0
0
合 計 | [6 empty] | 47714013 | 0 | 0 | 47714013
切りとり線

## 様式５_仕様書案 (3) (hidden)
機材仕様明細書
| 国名：ウクライナ国 | 案件名：ウクライナ国緊急復旧・復興プロジェクト向け機材（ヒートポンプ） | [8 empty] | 記入日：2023/11/15 Page： 1 /
| 機 材 名 | 仕 様 | メーカー名 | 数量 | JICSコメント／指摘根拠 | 指摘内容 | 見 積 書 価 格（円） |  |  |  | 備 考 | 松原コメント
採用価格
0 | 総則 | （総則） |  |  | 総則の記載
|  | 1. 中古品は認めない。 |  |  | 仕様書の言語表記について、英・和（メーカー名等）表記が混在しているので、どちらかに統一することをお勧めします。
2. 仕様欄において、「程度」と付記された数値は、その数値を中
心値として、±10％以内の範囲を認める。
3. 電源を必要とする機材の電源仕様は、単相AC230V、50Hz、
または内蔵ﾊﾞｯﾃﾘｰを使用するものとする。但し、各機材の
仕様欄に電源仕様の記載がある場合にはそれに従うこと。
4. 電源を必要とする機材については、仕様書に記載の有無にかか
わらず、機材を正常に作動させるために必要とされる資機材
（電源ｹｰﾌﾞﾙ、変換ﾌﾟﾗｸﾞ、電圧変換器など）は、当該機材に
含め、契約締結時に内訳明細書に記載すること。
5. 単相の電源ﾌﾟﾗｸﾞﾀｲﾌﾟは、各機材の仕様欄に記載のとおりCﾀｲﾌﾟ
であること。機材の電源ﾌﾟﾗｸﾞが指定のﾀｲﾌﾟに対応
できない場合は、変換ﾌﾟﾗｸﾞの使用を認める。
6. 電源を必要とする機材は、当該機材が現地 電源電圧に対応
できない場合、当該機材が正常に作動するために必要な定格容量を
満たすﾄﾗﾝｽを含めること。ﾄﾗﾝｽを含める場合、
契約内訳書作成時に個々のﾄﾗﾝｽのﾒｰｶｰ名、型式、型番、および
仕様（入出力電圧、定格容量など）を明記すること。
7. ﾒｰｶｰ設定の標準付属品は、仕様欄に記載がなくとも当該機材の
付属品として含め、契約内訳書作成時に個々のﾒｰｶｰ名、型式、
型番、および数量などを明記すること。
8. 機材を設置し、同機材が正常に作動するために必要な資機材
(据え付け部材、電源ｹｰﾌﾞﾙ、ﾄﾗﾝｽなど)は、仕様欄に記
載がなくとも当該機材に含めること。
9. 本件は納入前立会検査と技師派遣業務完了時検査を一括で
行い、費用の支払いは検査が完了した時点で請求可能とする。
10. 受注者は、仕向地における立会検査の際、ｵﾝﾗｲﾝで立ち会う
こと。
11. 機材引渡し後1年間の保証を付すること。
12. Declaration of Conformity (DoC）取得済みの機材または、
納入前に取得し、納入すること。
1 | Air Source Heat Pump Water Heater | General Description and function：Hot Water Heater |  |  | 機材名は（調達機材総括表の機材名欄に記載されている）一般的な機材名称を記載（なお、銘柄名はWH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit)である点に注意） Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | WH-SXC16H9E8 (Indoor unit), WH-UX16E8(Outdoor unit)→Air Source Heat Pump Water Heater Quantity：1 unit→削除 パナソニック㈱→削除 23→削除 C14にC18の内容を移動 | 44391748 |  |  | 44391748
|  | Specifications Type：Split type air source heat pump water heater Heating Capacity：Not less than 16kW Coefficient of Performance： 2.49 or surperior at Air temp. -7°C and Water temp. 35 °C 1.86 or surperior at Air temp. -7°C and Water temp. 55 °C Max. temperature of hot water supply：Not less than 55℃ Refrigerant：Hydrofluorocarbons ODP(ozone depletion potential)：0 Electrical Characteristic：Three Phase 380V 50Hz |  |  | A2WがAir Source Heat Pump Water Heaterを指している場合、不要。削除。 Manufacturer：はメーカー名の項があるので不要。削除。 | A2W→削除 Manufacturer：Panasonic or Equivalent→削除 C15にC19の内容を移動
|  | Accessory Hot water circulating pump（VFD Driven） |  | 必要数量記載 | 確認対象外
PCB( Power Control Board)
Base pan heater
3 way valve for DHW tanks
Aquarea Smart Cloud
10 m extension cable
Heat pumps group controller
Modbus interface
Sensors kit with cables（Outdoor ambient, Buffer tank, Zone water.）
Outdoor base ground support
Tray for condenser water compatible
Outdoor elevation platform
外機連結システム（５台） 概要 Reference Model：Cascade Manager PAW-A2W-CMH-2
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual（To be provided in Ukrainian or English）
Parts catalog（To be provided in Ukrainian or English）
|  | Reference Model：WH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit) | パナソニック㈱ | 23 | 参考銘柄は仕様の後に記載する。 メーカー名を記載 数量を記載 | Reference Model：WH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit) パナソニック㈱ 23
[5 empty] | 参考銘柄を記載 メーカー名を記載 数量を記載 | Reference Model：Cascade Manager PAW-A2W-CMH-2 パナソニック㈱ 5 | [5 empty] | C20に付属品として追記
2 | Air Purification Unit | General Description and function：Air purification unit |  |  | 機材名は一般的な機材名称を記載（なお、銘柄名はFV-15CSD1である点に注意） Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | FY-15CSD1→Air Purification Unit Quantity：1 unit→削除 パナソニック㈱→削除 10→削除 | 316410 |  |  | 316410
|  | Specifications Type：Ionization Air Purification Unit with Humidifying function Installation：Ceiling mounted Air flow rate：Not less than 15m3/hour Noise level：Less than 28 dB(A) at 1.0 meter remote Electrical Characteristic：Single phase 220V 50Hz |  |  | スペース、コロンなどの整理 | Specifications Type：Ionization Air Purification Unit with Humidifying function Installation：Ceiling mounted Air flow rate：Not less than 15m3/hour Noise level：Less than 28 dB(A) at 1.0 meter remote Electrical Characteristic：Single phase 220V 50Hz
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual：To be provided in Ukrainian or English
|  | Reference Model：FV-15CSD1 | パナソニック㈱ | 10 | 参考銘柄は仕様の後に記載する。（32行目参照） メーカー名を記載 数量を記載 | Reference Model：FV-15CSD1 パナソニック㈱ 10
3 | Split type Heat Pump Air Conditioner | General Description and function：Air Conditioners |  |  | 機材名は一般的な機材名称を記載 Quantity：1 unitは記載しない。 メーカー名は削除 数量を削除 | CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit)→Split type Heat Pump Air Conditioner Quantity：1 unit→削除 パナソニック㈱→削除 5→削除 | 1344725 |  |  | 1344725
|  | Specifications： Type Split type air -air heat pump air conditioner Indoor Unit Type Wall mounted Heating Capacity Not less than 4.3kW （Outdoor air condition: at－20℃） Outdoor Unit Coefficient of Performance Not less than 2.56 at Air temp. -7°C Refrigerant Hydrofluorocarbons: ODP(ozone depletion potential) = 0 Electrical Characteristic Single phase 220V 50Hz |  |  | スペース、コロンなどの整理 Heating Capacityの（Outdoor air condition: at-20℃）の記載意図不明。外気温に関係なく機材のHeating Capacityは4.3kWでは。 | Specifications： Type：Split type air -air heat pump air conditioner Indoor Unit Type：Wall mounted Heating Capacity：Not less than 4.3kW Outdoor Unit Coefficient of Performance：Not less than 2.56 at Air temp. -7°C Refrigerant：Hydrofluorocarbons ODP(ozone depletion potential)：0 Electrical Characteristic：Single phase 220V 50Hz
|  | Accessory： Remote controller：Built-in Wi-Fi interface |  |  | 確認対象外
Refrigerant pipe：Liquid and gas piping with insulation
Outdoor base ground support
Outdoor elevation platform
Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation
Manuals Operation manual：To be provided in Ukrainian or English
|  | Reference Model：CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) | パナソニック㈱ | 5 | 参考銘柄は仕様の後に記載する。（44行目参照） メーカー名を記載 数量を記載 | Reference Model：CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) パナソニック㈱ 5
0
0
合 計 | [6 empty] | 46052883 | 0 | 0 | 46052883

## 掲載版_様式５_仕様書案
機材仕様明細書
| 国名：ウクライナ国 | 案件名：ウクライナ国緊急復旧・復興プロジェクト向け機材（ヒートポンプ）
| 機 材 名 | 仕 様 | メーカー名 | 数量
0 | 総則 | （総則）
1. 中古品は認めない。
2. 仕様欄において、「程度」と付記された数値は、その数値を中
心値として、±10％以内の範囲を認める。
3. 電源を必要とする機材の電源仕様は、単相AC230V、50Hz、
または内蔵ﾊﾞｯﾃﾘｰを使用するものとする。但し、各機材の
仕様欄に電源仕様の記載がある場合にはそれに従うこと。
4. 電源を必要とする機材については、仕様書に記載の有無にかかわらず、
機材を正常に作動させるために必要とされる資機材
（電源ｹｰﾌﾞﾙ、変換ﾌﾟﾗｸﾞ、電圧変換器など）は、当該機材に含めること。
5. 単相の電源ﾌﾟﾗｸﾞﾀｲﾌﾟは、各機材の仕様欄に記載のとおりCﾀｲﾌﾟ
であること。機材の電源ﾌﾟﾗｸﾞが指定のﾀｲﾌﾟに対応できない場合は、
変換ﾌﾟﾗｸﾞの使用を認める。
6. ﾒｰｶｰ設定の標準付属品(据え付け部材、電源ｹｰﾌﾞﾙ、ﾄﾗﾝｽなど）及び同機材が
１年間、または3,000時間正常に作動するために必要な消耗品やｽﾍﾟｱﾊﾟｰﾂは、
仕様欄に記載がなくとも当該機材の付属品として含め、契約内訳書作成時に
個々のﾒｰｶｰ名、型式、などを明記すること。
7. 本件は納入前立会検査と技師派遣業務完了時検査を一括で
行い、費用の支払いはサイトごとに検査が完了した時点で請求可能とする。
8. 仕向地における立会検査の際、受注者担当者はｵﾝﾗｲﾝで立ち会うことを認める。
現地では派遣技師が立ち会うこととする。
9. 機材引渡し後1年間の保証を付すること。
10. Declaration of Conformity (DoC）取得済みの機材または、
納入前に取得し、納入すること。
1 | Air Source Heat Pump Water Heater | General Description and function：Hot Water Heater
Specifications Type：Split type air source heat pump water heater Heating Capacity：Not less than 16kW Coefficient of Performance： 2.49 or surperior at Air temp. -7°C and Water temp. 35 °C 1.86 or surperior at Air temp. -7°C and Water temp. 55 °C Max. temperature of hot water supply：Not less than 55℃ Refrigerant：Hydrofluorocarbons ODP(ozone depletion potential)：0 Electrical Characteristic：Three Phase 380V 50Hz
|  | Accessory PCB( Power Control Board) |  | 23
|  | Base pan heater |  | 23
|  | 3 way valve for DHW tanks |  | 6
|  | Aquarea Smart Cloud |  | 23
|  | Modbus interface |  | 23
|  | Outdoor ambient sensor |  | 23
|  | Buffer tank sensor |  | 23
|  | Zone water seonsor |  | 23
|  | Outdoor base ground support |  | 23
|  | Tray for condenser water compatible |  | 23
|  | Temperature sensor kit Tank sensor with 6 m cable |  | 21
|  | Tank sensor with 6 m cable length |  | 2
|  | 外機連結システム Discription：Integrated group controller for Air source heat pump water heater a.) Function: Optimal group control of Air source heat pump water heaters and Communication capability with IP network b.) Human Machine Interface; Wall mounted touch screen displayc. c.) IP compatibility: Built-in Modbus IP |  | 5
|  | Spare parts, Consumables Consumables for 1 year or 3,000 hours' operation |  | 23
|  | Manuals Operation manual（To be provided in Ukrainian or English） |  | 23
|  | Reference Model：WH-SXC16H9E8 (Indoor unit), WH-UX16HE8(Outdoor unit) | パナソニック㈱ | 23
2 | Air Purification Unit | General Description and function：Air purification unit
Specifications Type：Ionization Air Purification Unit with Humidifying function Installation：Ceiling mounted Air flow rate：Not less than 15m3/hour Noise level：Less than 28 dB(A) at 1.0 meter remote Electrical Characteristic：Single phase 220V 50Hz
|  | Manuals Operation manual：To be provided in Ukrainian or English |  | 10
|  | Reference Model：FV-15CSD1 | パナソニック㈱ | 10
3 | Split type Heat Pump Air Conditioner | General Description and function：Air Conditioners
Specifications： Type Split type air -air heat pump air conditioner Indoor Unit Type Wall mounted Heating Capacity Not less than 4.3kW （Outdoor air condition: at－25℃） Outdoor Unit Coefficient of Performance Not less than 2.56 at Air temp. -7°C Refrigerant Hydrofluorocarbons: ODP(ozone depletion potential) = 0 Electrical Characteristic Single phase 220V 50Hz
|  | Accessory： Remote controller：Built-in Wi-Fi interface |  | 5
|  | Refrigerant pipe：Liquid and gas piping with insulation |  | 5
|  | Outdoor base ground support |  | 5
|  | Manuals Operation manual：To be provided in Ukrainian or English |  | 5
|  | Reference Model：CS-HZ35XKE (Indoor unit), CU-HZ35XKE(Outdoor unit) | パナソニック㈱ | 5
Note on E48: 作成者: １サイト3部＋PDFデータでしょうか？