## Sheet1
Technical Specifications
Item No. | Name of Equipment | Description (Required by Employer) | Proposed by Competitor | Note
(e.g.) | Surge Arrester ●● kV | 1. General technical descriptions
|  | 1.1 Standard : IEC 600●●-●:● | Comply
|  | 1.2 Manufacturer : * | ●● Co., Ltd.
|  | 1.3 Conditional denotation (brand) : * | △△
|  | 1.4 Rated voltage, kV : ●● | Comply
|  | 1.5 Maximum operating system voltage, kV : ●● | Comply
|  | 1.6 SA rated voltage, kV, not less: ●● | Comply
1 | Surge Arrester 330 kV | 1. General technical descriptions
1.1 Standard : IEC 60099-4:2014
1.2 Manufacturer : *
1.3 Conditional denotation (brand) : *
1.4 Rated voltage, kV : 330
1.5 Maximum operating system voltage, kV : 363
1.6 SA rated voltage, kV, not less: 288
1.7 Maximum allowable continuous operating voltage,
kV, not less : 230
1.8 Rated discharge current, kA, not less : 20
1.9 Line grade class as per IEC : 2
1.10 Specific energy intensity, kJ/kV Ur : *
2. Values of climatic factors of environment:
2.1 Location category : 1
2.2 Operating temperature range, ℃ : from -40 to +40
2.3 Ice thickness, mm : 22
2.4 Wind velocity under ice conditions, m/s : 22
2.5 Wind velocity without ice conditions, m/s : 28
2.6 Maximum installation altitude, m : 1000
2.7 Area's seismic stability, not less, MSK-64 points
Or equivalent (Seismic acceleration: 50gal) : 6
Seismic acceleration: 50gal
2.8 Atmospheric pollution rate at substation's location
area, according to IEC 60815-2008 : C
2.9 Specific creepage distance of external insulation,
according to IEC 60815-2008, mm/kV : 34,7
3. Insulation electrical strength requirements,
including:
3.1 Residual voltage, kV, not more than:
3.1.1 at current impulse (1/2 µs) 10 kA : *
3.1.2 at switching impulse of current (30/60 µs) 1 kA
: *
3.1.3 at switching impulse of current (30/60 µs) 2 kA
: *
3.1.4 at lightning impulse of current (8/20 µs) 5 kA
: *
3.1.5 at lightning impulse of current (8/20 µs) 10 kA
: *
3.1.6 at lightning impulse of current (8/20 µs) 20 kA
: *
3.2 Short-circuit through current, kA :
3.2.1 Short-circuit currents stability, not less, kA
: 25
|  | 3.2.2 Short curcuit duration, sec : 0.2 |  | （As per IEC60099-4）
4. Design, manufacturing and materials requirements
4.1 Type of neutral terminal grounding
: Solidly-grounded
4.2 Permissible wires stress, N, not less than : 1000
4.3 External insulation (material/coating colour)
: white coloured / gray
4.4 Power terminal lead : Al
4.5 Surge counter with possibility of measuring of
leakage current (0-5 mArms, including active
part) (yes, no) : Yes
4.6 Insulated base for installation of SA condition
monitoring device (yes, no) : Yes
4.7 Design : explosion- and fire-proof
4.8 Possibility of connection to SA (power equipment
monitoring system) with controlling of the
following parameters : Yes
4.8.1 SA operation recording : Yes
4.8.2 Operation time recording : Yes
4.8.3 Recording of value of impulse of SA transit
current : Yes
5. Reliability requirements:
5.1 Service lifetime, years, not less : 30
Note: Lifecycle considered when designing
(This is NOT warranty condition)
5.2 Warranty period: from the date of its receipt at the
designated delivery place, years, not less than : 1
6. SA scope of supply
6.1 Assembled SA according to specification : Yes
6.2 Shading rings for corona protection and provision
of voltage distribution uniformity : Yes
6.3 SA condition monitoring equipment : Yes
6.4 Maintenance documentation, set : Yes
6.5 Technical passport (printed document with
technical data) : For each SA
6.6 Installation and maintenance manual and drawings
: 1 copy per SA
6.7 Kitting list (List of all parts (main and spare)
to be included in the delivery) : For each SA
6.8 Factory tests reports : For each SA
* Data provided by the manufacturer
2 | Surge Arrester 220 kV | 1. General technical descriptions
1.1 Standard : IEC 60099-4:2014
1.2 Manufacturer : *
1.3 Name / Type : *
1.4 Rated voltage, kV : 220
1.5 Maximum operating system voltage, kV : 245
1.6 SA rated voltage, kV, not less : 192
1.7 Maximum allowable continuous operating voltage,
kV, not less : 160
1.8 Rated discharge current, kA, not less : 10
1.9 Line grade class as per IEC : 2
1.10 Specific energy intensity, kJ/kV Ur : *
2. Values of climatic factors of environment:
2.1 Location category : 1
2.2 Operating temperature range, ℃ : from -40 to +40
2.3 Ice thickness, mm : 22
2.4 Wind velocity under ice conditions, m/s : 22
2.5 Wind velocity without ice conditions, m/s : 28
2.6 Maximum installation altitude, m : 1000
2.7 Area's seismic stability, not less, MSK-64 points
Or equivalent (Seismic acceleration: 50gal) : 6
Seismic acceleration: 50gal
2.8 Atmospheric pollution rate at substation's
location area, according to IEC 60815-2008 : C
2.9 Specific creepage distance of external insulation,
according to IEC 60815-2008, mm/kV : 34,7
3. Insulation electrical strength requirements:
3.1 Residual voltage, kV, not more than :
3.1.1 at current impulse (1/2 µs) 10 kA : *
3.1.2 at switching impulse of current (30/60 µs) 1 kA
: *
3.1.3 at switching impulse of current (30/60 µs) 2 kA
: *
3.1.4 at lightning impulse of current (8/20 µs) 5 kA
: *
3.1.5 at lightning impulse of current (8/20 µs) 10 kA
: *
3.1.6 at lightning impulse of current (8/20 µs) 20 kA
: *
3.2 Short-circuit through current,kA:
3.2.1 Short-circuit currents stability, not less, kA
: 25
3.2.2 Short cuircuit duration, sec : 0.2
According with IEC60099-4
4. Design, manufacturing and materials requirements
4.1 Type of neutral terminal grounding
: Solidly-grounded
4.2 Permissible wires stress, N, not less than : 2500
4.3 External insulation (material/coating colour)
: polymer white /gray
4.4 Power terminal lead : Al
4.6 Insulated base for installation of SA condition
monitoring device : Yes
4.7 Design : explosion- and fire-proof
5. Reliability requirements:
5.1 Service lifetime, years, not less : 30
Note: Lifecycle considered when designing (This
is NOT warranty condition.)
5.2 Warranty period: from the date of its receipt at the
designated delivery place, years, not less than : 1
6. SA scope of supply
6.1 Assembled SA according to specification : Yes
6.2 Shading rings for corona protection and provision
of voltage distribution uniformity : If necessary
6.3 Surge counter with possibility of measuring of
leakage current (0-5 mArms, including active part)
: Yes
6.4 Maintenance documentation, set : Yes
6.5 Technical passport (printed document with
technical data) : For each SA
6.6 Installation and maintenance manual and drawings
: 1 copy per SA
6.7 Kitting list (List of all parts (main and spare)
to be included in the delivery) : For each SA
6.8 Factory tests reports : For each SA
* Data provided by the manufacturer
3 | Surge Arrester 150 kV | 1. Manufacturer designation : **
2. Standard : IEC 60099-4:2014
3. Type : **
4. Installation : Outdoor
5. Network frequency : 50Hz
6. System Nominal Voltage : 150kV
7. Surge arrester rated voltage, not less : 138kV
8. Maximum allowable continuous operating voltage
: 120kV*
9. Nominal discharge current, not less : 10kA
10. Line grade class as per IEC : 3
11. Insulation : Polymer, white or silver- white or
Gray
12. Min. lifetime of equipment : 30years
Note: Lifecycle considered when designing (This
is NOT warranty condition.)
13. Terminal lead : Al
14. Rated withstand short-circuit current, not less,
kA :40kA
Scope of supply
15. Surge arrester with line terminal clamp,
grounding clamp and insulating base, (yes, no)
: yes
16. Availability of contact terminals for fixing
hardware clamps (sizes to be specified), (yes, no)
: yes
17. Shading rings for voltage distribution
(if necessary), (yes, no) : *
18. Surge counter with possibility of measuring of
leakage current (0-5 mArms, including active
part) : yes
19. Operational and Maintenance (O&M) documentation
in English and Ukrainian language, (yes, no) : yes
20. Set of metallic support structures
(sizes and design shall be additionally
specified),(yes, no) : yes
21. Technical passport (printed document with
technical data), Rating plate (yes, no) : yes
22. Factory acceptance tests reports, (yes, no) : yes
23. Operating manuals or guidelines, (yes, no) : yes
24. Installation drawings with installation manual
: yes
25. Certificate of compliance, (yes, no) : yes
* Data provided by the manufacturer
** Data provided by the manufacturer
4 | Surge Arraster 110 kV | 1. General technical descriptions
1.1 Standard : IEC 60099-4:2014
1.2 Manufacturer : *
1.3 Conditional denotation (brand) : *
1.4 Rated voltage, kV : 110
1.5 Maximum operating system voltage, kV : 126
1.6 SA rated voltage, kV, not less : 108
1.7 Maximum allowable continuous operating voltage,
kV, not less : 83
1.8 Rated discharge current, kA, not less : 10
1.9 Line grade class as per IEC : 2
1.10 Specific energy intensity, kJ/kV Ur : *
2. Values of climatic factors of environment:
2.1 Location category : 1
2.2 Operating temperature range, ℃ : from -40 to +40
2.3 Ice thickness, mm : 22
2.4 Wind velocity under ice conditions, m/s : 22
2.5 Wind velocity without ice conditions, m/s : 28
2.6 Maximum installation altitude, m : 1000
2.7 Area's seismic stability, not less, MSK-64 points
Or equivalent (Seismic acceleration: 50gal) : 6
Seismic acceleration: 50gal
2.8 Atmospheric pollution rate at substation's
location area, according to IEC 60815-2008 : C
2.9 Specific creepage distance of external insulation,
according to IEC 60815-2008, mm/kV : 34,7
3. Insulation electrical strength requirements,
including:
3.1 Residual voltage, kV, not more than:
3.1.1 at current impulse (1/2 µs) 10 kA : *
3.1.2 at switching impulse of current (30/60 µs) 1 kA
: *
3.1.3 at switching impulse of current (30/60 µs) 2 kA
: *
3.1.4 at lightning impulse of current (8/20 µs) 5 kA
: *
3.1.5 at lightning impulse of current (8/20 µs) 10 kA
: *
3.1.6 at lightning impulse of current (8/20 µs) 20 kA
: *
3.2 Short-circuit through current, kA:
3.2.1 Short-circuit currents stability, not less, kA
: 25
|  | 3.2.2 Short cuircuit duration, sec : 0.2 |  | (As per IEC60099-4)
4. Design, manufacturing and materials requirements
4.1 Type of neutral terminal grounding
: Solidly-grounded
4.2 Permissible wires stress, N, not less than : 500
4.3 External insulation (material/coating colour)
: preferably (white coloured)
4.4 Power terminal lead : Al
4.5 Surge counter with possibility of measuring of
leakage current (0-5 mArms, including active
part) (yes, no) : Yes
4.6 Insulated base for installation of SA condition
monitoring device (yes, no) : Yes
4.7 Design : explosion- and fire-proof
4.8 Possibility of connection to SA (power equipment
monitoring system) with controlling of the
following parameters : Yes
4.8.1 SA operation recording : Yes
4.8.2 Operation time recording : Yes
4.8.3 Recording of value of impulse of SA transit
current : Yes
5. Reliability requirements:
5.1 Service lifetime, years, not less : 30
Note: Lifecycle considered when designing (This
is NOT warranty condition.)
5.2 Warranty period: from the date of its receipt at the
designated delivery place, years, not less than : 1
6. SA scope of supply
6.1 Assembled SA according to specification : Yes
6.2 Shading rings for corona protection and provision
of voltage distribution uniformity (if necessary)
: *
6.3 SA condition monitoring equipment : Yes
6.4 Maintenance documentation, set : Yes
6.5 Technical passport (printed document with
technical data) / Name plate : For each SA
6.6 Installation and maintenance manual and drawings
: 1 copy per SA
6.7 Kitting list (List of all parts (main and spare)
to be included in the delivery) : For each SA
6.8 Factory tests reports : For each SA
* Data provided by the manufacturer
5 | Surge Arraster 35 kV | 1. General technical descriptions
1.1 Standard : IEC 60099-4:2014
1.2 Manufacturer : *
1.3 Conditional denotation (brand) : *
1.4 Rated voltage, kV : 35
1.5 Maximum operating system voltage, kV : 40,5
1.6 SA rated voltage, kV, not less : 51
1.7 Maximum allowable continuous operating voltage,
kV, not less : 41
1.8 Rated discharge current, kA, not less : 10
1.9 Line grade class as per IEC : 2
1.10 Specific energy intensity, kJ/kV Ur : *
2. Values of climatic factors of environment:
2.1 Location category : 1
2.2 Operating temperature range, ℃ : from -34 to +36
2.3 Ice thickness, mm : 22
2.4 Wind velocity under ice conditions, m/s : 22
2.5 Wind velocity without ice conditions, m/s : 28
2.6 Maximum installation altitude, m : 1000
2.7 Area's seismic stability, not less, MSK-64 points
Or equivalent (Seismic acceleration: 50gal) : 6
Seismic acceleration: 50gal
2.8 Atmospheric pollution rate at substation's
location area, according to IEC/TS 60815-1:2008 : C
2.9 Specific creepage distance of external
insulation, according to IEC/TS 60815-1:2008,
mm/kV : 41,0
3. Insulation electrical strength requirements,
including:
3.1 Residual voltage, kV, not more than:
3.1.1 at current impulse (1/2 µs) 10 kA : *
3.1.2 at switching impulse of current (30/60 µs) 1 kA
: *
3.1.3 at switching impulse of current (30/60 µs) 2 kA
: *
3.1.4 at lightning impulse of current (8/20 µs) 5 kA
: *
3.1.5 at lightning impulse of current (8/20 µs) 10 kA
: *
3.1.6 at lightning impulse of current (8/20 µs) 20 kA
: *
3.2. Short-circuit through current, kA:
3.2.1 Short-circuit currents stability, not less, kA
: 20
3.2.2 Short cuircuit duration, sec : 0.2
4. Design, manufacturing and materials requirements
4.1 Type of neutral terminal grounding : Isolated
4.2 Permissible wires stress, N, not less than : 300
4.3 External insulation (material/coating colour) :
white coloured / gray
4.4 Power terminal lead : Al
4.7 Design : explosion- and fire-proof
5. Reliability requirements
5.1 Service lifetime, years, not less : 30
Note: Lifecycle considered when designing (This
is NOT warranty condition.)
5.2 Warranty period:from the date of its receipt at the
designated delivery place, years, not less than : 1
6. SA scope of supply
6.1 Assembled SA according to specification : Yes
6.2 Maintenance documentation, set : Yes
6.3 Technical passport (printed document with
technical data) / Name plate : For each SA
6.4 Installation and maintenance manual and drawings
: 1 copy per SA
6.5 Kitting list (List of all parts (main and spare)
to be included in the delivery) : For each SA
6.6 Factory tests reports : For each SA
* Data provided by the manufacturer
6 | 110 kV Circuit Breaker | 1. Standard : IEC 62271-100 and other IEC standards,
valid at the date of equipment manufacture
2. Manufacturer : *
3. Name / Type : *
4. Rated voltage, kV : 110
5. Maximum operating voltage, kV : 126
6. Rated frequency, Hz : 50
7. Rated current, A, not less : 3150
8. Rated breaking current, kA, not less : 40
9. Values of climatic factors of environment:
Location category : 1
Operating temperature range, ℃ : -40 up to +40
Ice thickness, mm : 19
Maximum installation altitude, m : up to 1000
Area's seismic stability, not less, MSK-64 points
: 7
10. Atmospheric pollution rate at substation's
location area, according to IEC/TS 60815-1:2008
: C
Specific creepage distance of external
insulation, according to IEC/TS 60815-1:2008,
mm/kV : 34,7
11. Rated lightning impulse withstand voltage, Up, kV
(peak value)
- across poles : 520
Rated short-duration power-frequency withstand
voltage, kV
- across breakers poles : 230
12. Short-circuit through current, kA:
Periodic component initial rms value, kA, not less
: 40
Root-mean-square value of current within its
duration (short-time withstand current), kA,
not less than : 40
Short-time withstand current duration time, s : 1
13. Switching capacity requirements:
Maximum peak (short-time electrodynamic current),
kA, not less : 102
Rated content of aperiodic component in the
short-circuit current, %, not less : *
CB opening time, s, maximum : 0,04
Total opening time, s, maximum : 0,05
Rated out of phase breaking current Id, kA :
25% І br.cur.
Non-load line current, which stops without
restrike, minimum, A : 31,5
Operating duty cycles : O-0,3c-CO-180c-CO
Maximum time interval between first and last
pole, s, max:
when closing : 0,01
when opening : 0,01
Minimum dead time for auto-reclosing, s : 0,3
Switching endurance lifetime (amount of O and C
operations) under short-circuit currents, minimum
from 60 to 100% of I rated breaking current : 20
from 30 to 60% of I rated breaking current : 34
14. Design, manufacture and materials requirements:
Design : Live-tank, three-pole, explosion- and
fire-proof
Quantity of interrupter per pole : *
Permissible terminals load N, minimum : 1000
Insulating medium : SF6 (gas mixture)
Power terminal lead : Aluminium clamp*
Height from foundation to busbar clamp, mm,
not less : *
Rated annual SF6 leakage, % maximum : 0,5
External insulation (material/coating colour)
: Porcelain/ Polymer*
All steel parts of the circuit breaker that are
subject to outdoor environmental impact shall
have durable corrosion-resistant coating or
shall be made of corrosion-resistant materials
(yes, no) : yes
15. Technical parameters of the operating mechanism
Rated voltage of closing and opening circuits, V
: 220 DC
Power supply voltage of closing spring-setting
motor, V : 220 AC
Control circuit voltage operating range, % of the
rated voltage
- closing circuit : 85-110
- opening circuit : 70-110
Quantity of opening coils, pcs : 2
Quantity of closing coils, pcs : 1
Number of CB position auxiliary contacts
(NO/NC/pulse) : 12/12
Power supply voltage of heaters, V : 220 AC
Operating mechanism type : spring
16. Instruments and maintenance devices:
CB operations counter : yes
Switching lifetime accounting device : yes
Monomeric indicator of SF6 density with temperature
compensation and interlock for signalling on
pressure decreasing and inhibition of CB control :
yes
Mechanical Open/Close position indicator : yes
CB's local control buttons : yes
Control cabinet heating circuits failure
indicator : yes
Interlocking relay of CB multiple switching : yes
Control type switch - local/remote : yes
17. Possibility of connection to SAS (monitoring
system) with controlling of the following
parameters:
SF6 gas (mixture) pressure : yes
air temperature in motor drive cabinet : yes
coil impulse (closing and opening solenoid) : yes
switching time: closing and opening : yes
breaking current : yes
Main contacts wearing status with controlling of
the following parameters : yes
CB status signalling: closed, open : yes
CB monitoring system status signalling : yes
18. Control mode : Three-phase
19. Quantity of operating mechanisms, pcs : 1
20. Quantity of poles, pcs : 3
21. Scope of supply:
Cables for internal wiring (between control
cabinet operating mechanisms, synchronization
unit and etc.) : Yes**
Set of steel structures with anchors bolts with
corrosion-resistant coating. : Yes
Central (main) control cabinet : 1
Kitting list (List of all parts (main and spare)
to be included in the delivery) : Yes
SF6 (gas mixture) cylinder(s) in amount necessary
for first re-filling of the circuit-breakers up
to rated pressure : Yes
Set of CB sensors : For each pole
Installation and maintenance manual and drawings
: Yes
Certificate of conformity : Yes
Factory tests reports : Yes
Spare parts and accessories according to kitting
list, set : 1
Operational documentation, number of copies : 1
22. CB service life, years, not less than : 30
23. Mechanical withstand lifetime of cycles at C-t-O,
Class M2 as per IEC : 10000
24. Mechanical withstand lifetime at load currents of
up to 100% Ir, C-t-O, not less : 10000
* data shall be provided by the manufacturer
7 | 110kV Current | 1. Standard : IEC 61869-1, IEC 61869-2 and other IEC
| Transformer | standards
2. Manufacturer : *
3. Name / Type : *
4. Rated voltage, kV : 110
5. Maximum rated voltage, kV : 126
6. Rated frequency, Hz : 50
7. Values of climatic factors of environment:
Location category : 1
Operating temperature range, ℃ : from -40 to +40
Ice thickness, mm : 19
Maximum installation altitude, m : Up to 1000
Area's seismic stability, not less, MSK-64 points
: 6
8. Atmospheric pollution rate at substation's
location area, according to IEC 60815-2008 : C
Specific creepage distance of external insulation,
mm/kV : 34,7
9. Short-circuit currents withstand capacity:
Short-circuit current duration, s : 1
Rated short-time thermal currents and short-time
electrodynamic currents І d/ І t, kA, not less
than : 78,75/31,5
10. Rated value of primary currents, A / Rated
secondary current, A : 1500
11. Maximum admissible thermal withstand continuous
primary current, not less than, A (I cth)
: 120% Ін
12. Rated secondary current, A : 5*
13. Quantity of secondary windings : 6*
Winding No. 1, 2. Accuracy class, % : 0,2S
Rated load, VA : 20*
Winding No. 3-6. Accuracy class, % : 10P
Rated load, VA : 30*
14. Magnetic saturation voltage, not less than, V
: 300
15. Insulation electrical strength requirements:
Lightning impulse withstand voltage to ground,
not less, kV : 450
Short-duration power-frequency withstand voltage
to ground, not less, kV : 230
16. Design, manufacturing and materials requirements:
Permissible wires stress, N, not less than : 1000
Dielectric (insulation and extinguishing medium)
: SF6 (gas mixture)
Rated permissible SF6 (gas mixture) leakage level,
% per year, % of SF6 (gas mixture) weight, not
more than : 0,5
External insulation (material/coating colour)
: Polymer
Transformer ratio switching : On the primary side
17. Safety ratio of instruments of measuring
winding, not more than : 10
18. Rated multiplication factor of secondary winding
for protection, not less : 20
19. Shall be equipped with SF6 gas (gas mixture)
pressure monitoring devices (densimeters)
depending on air temperature : yes
20. CT service life, years, not less than : 30
21. Scope of supply
Assembled current transformer : yes
Maintenance documentation : yes
Technical passport : For each CT
Installation and maintenance manual and drawings
: 1 copy for three CT
Set of fastening for primary leads : For each CT
Kitting list (List of all parts (main and spare)
to be included in the delivery) : For each CT
Cylinders with SF6 gas (gas mixture) for initial
filling up to rated pressure : yes
Factory test reports : For each CT
Certificate of conformance : yes
* data shall be provided by the manufacturer
8 | 330kV Disconnector | 1. Standard : IEC 62271-102 and other IEC
standards, valid at the date of equipment
manufacture
2. Manufacturer : *
3. Version (make) : *
4. Rated voltage, kV : 330
5. Maximum operating voltage, kV : 362
6. Rated frequency, Hz : 50
7. Rated current, A, not less : 3150
8. Values of climatic factors of environment:
- Location category : 1
- Operating temperature range, ℃ : From -40 to +40
- Ice thickness, mm : 22
- Maximum installation altitude, m : Up to 1000
- Area's seismic stability, not less, MSK-64 points
: 6
9. Atmospheric pollution rate at substation's location
area, according to IEC 60815-2008 : C
Specific creepage distance of external insulation,
according to IEC 60815-2008, mm/kV : 34,7
10. Requirement to dielectric strength of insulation,
including:
Full lightning impulse withstand voltage, kV:
- Phase to ground : 1050
- across terminals : 1255
Switching Impulse withstand voltage KV
- Phase to ground : 850
- Across terminals : 950
Short-duration withstand power-frequency voltage,
kV:
- Phase to ground : 460
- across open terminals : 575
11. Requirements to short-circuit through current
withstand:
Rated peak withstand current, kA, not less than
: 50
Initial effective value of periodic component, kA,
not less than : 20
Root-mean-square value of current within its
duration (short-time withstand current), kA,
not less than : 20
Allowable short-time withstand current duration
for main circuit,s : 2
Allowable short-time withstand current duration
for grounding circuit,s : 1
12. Mechanical endurance, number of C-cycles : 10000
13. Control mode : Three-phase
14. Design, manufacturing and materials requirements::
Permissible wires stress, N, not less than : 1500
Type of construction arrangement
: Semi-pantograph with horizontal break
Design : Single-pole
Quantity of earting switch
: with one earting switch
: with two earting switches
Insulators of support columns and rotary columns
(material/coating colour) : Porcelain/ *
Power terminal leads : *
Corrosion-inhibiting coating of steel parts
(hot zinc, thermodiffusion zinc) : Yes
Availability of interlocking between main contact
blades and earthing knives:
- electrical interlocking : Yes
- mechanical interlocking : Yes
- electromagnetic interlocking : Yes
15. Operating mechanism requirements:
Operating mechanism type for main circuit
: electromotor
for grounding circuit
Rated voltage of electrical motor supply, V
: ～380, 50 Hz
Operating range of operating mechanism voltage,
%Urat : 85-110
Availability of protection of operating
mechanism's electrical motor : Yes
Availability of protection of secondary circuit
: Yes
Availability of control switch (local / remote)
: Yes
Availability of manual control of operating
mechanism : Yes
Availability of disconnector's local control
buttons : Yes
Supply voltage of interlocking system and remote
control circuits,V : =220
Supply voltage of local control circuits,V : =220
Number of free normally open (NO) auxiliary
contacts
- of main blades : 12
- of earthing switch : 12
Number of free normally closed (NC) auxiliary
contacts
- of main blades : 12
- of earthing switch : 12
Operating mechanism's cabinet shall be made from
corrosion-preventing material : Yes
16. Scope of supply:
Set of steel support stands for disconnector with
corrosion-preventing coating : Yes
Individual SPTA kit : Yes
Maintenance documentation in Russian or Ukrainian
language, set : Yes
Technical passport : For each disconnector
Installation and maintenance manual and drawings
: For each disconnector
Kitting list (List of all parts (main and spare)
to be included in the delivery)
: For each disconnector
Factory tests reports : For each disconnector
17. Height from foundation of fixing of operating
mechanism, mm : ～1200
18. Service life, years : 30
9 | 330 kV Circuit Breaker | 1. Standard : IEC 62271-100 and other IEC standards,
valid at the date of equipment manufacture
2. Manufacturer : *
3. Name / Type : *
4. Rated voltage, kV : 330
5. Maximum operating voltage, kV : 362
6. Rated frequency, Hz : 50
7. Rated current, A, not less : 3150
8. Rated breaking current, kA, not less : 40
9. Values of climatic factors of environment:
Location category : 1
Operating temperature range, : -40 up to +40
Ice thickness, mm : 22
Maximum installation altitude, m : up to 1000
Area's seismic stability, not less, MSK-64 points
: 7
10. Specific creepage distance of external insulation,
according to IEC 60815-2008, mm/kV, not less : 34,7
Atmospheric pollution rate at substation's location
area, according to IEC 60815-2008 : C
11. Requirement to dielectric strength of insulation
(DSTU IEC 60071-1) including:
Rated lightning impulse withstand voltage, Up,
kV (peak value)
- phase to earth : 1050
- across poles : 1255
Rated switching impulse withstand voltage, kV
- phase to earth : 850
- across breakers poles : 950
Rated short-duration power-frequency withstand
voltage, kV
- phase to earth : 460
- across breakers poles : 575
12. Short-circuit through current, kA:
Periodic component initial rms value,
kA, not less : 40
Root-mean-square value of current within its
duration(short-time withstand current),
kA, not less than : 40
Short-time withstand current duration time,s : 3
13. Switching capacity requirements:
Maximum peak (short-time electrodynamic current),
kA, not less : 102
Rated content of aperiodic component in the
short-circuit current, %, not less : 45
CB opening time, s, maximum : 0,04
Total opening time, s, maximum : 0,05
Rated out of phase breaking current Id, kA
: 25% I br.cur
Non-load line current, which stops without
restrike, minimum, A : 315
Operating duty cycles : O-0,3c-CO-180c-CO
Maximum time interval between first and last
pole, s, max:
when closing : 0,01
when opening : 0,01
Minimum dead time for auto-reclosing, s : 0,3
Switching endurance lifetime (amount of O and C
operations) under short-circuit currents, minimum
from 60 to 100% of I rated breaking current : 20
from 30 to 60% of I rated breaking current : 34
14. Design, manufacture and materials requirements:
Design : Live-tank, single pole, explosion- and
fire-proof
Quantity of interrupter per pole : *
Permissible terminals load N, minimum : 1500
Insulating medium : SF6 (gas mixture)
Power terminal lead : Aluminium clamp*
Height from foundation to busbar clamp, mm, not
less : 6000
Rated annual SF6 leakage, % maximum : 0,5
External insulation (material/coating colour)
: Porcelain/ Polymer*
All steel parts of the circuit breaker that are
subject to outdoor environmental impact shall
have durable corrosion-resistant coating or shall
be made of corrosion-resistant materials
(yes, no) : yes
15. Technical parameters of the operating mechanism
Rated voltage of closing and opening circuits, V
: 220 DC
Power supply voltage of closing spring-set ting
motor, V : 220 AC
Control circuit voltage operating range, % of
the rated voltage
- closing circuit : 85-110
- opening circuit : 70-110
Quantity of opening coils, pcs : 2
Quantity of closing coils, pcs: 1
Number of CB position auxiliary contacts
(NO/NC) : 12/12
Power supply voltage of heaters, V : 220 AC
Operating mechanism type : spring
16. Instruments and maintenance devices:
CB operations counter : yes
Switching lifetime accounting device : yes
Monomeric indicator of SF6 density with
temperature compensation and interlock for
signalling on pressure decreasing and inhibition
of CB control : yes
Mechanical Open/Close position indicator : yes
CB's local control buttons : yes
Control cabinet heating circuits failure indicator
: yes
Interlocking relay of CB multiple switching : yes
Control type switch - local/remote : yes
17. Possibility of connection to SAS (monitoring
system)
with controlling of the following parameters:
SF6 gas (mixture) pressure : yes
air temperature in motor drive cabinet : yes
coil impulse (closing and opening solenoid) : yes
switching time: closing and opening : yes
breaking current : yes
Main contacts wearing status with controlling of
the following parameters : yes
CB status signalling: closed, open : yes
CB monitoring system status signalling : yes
18. Control mode : single-phase / three-phase
19. Quantity of operating mechanisms, pcs : 3
20. Quantity of poles, pcs : 3
21. Scope of supply:
Cables for internal wiring (between control
cabinet, operating mechanisms, synchronization
unit and etc.) : Yes**
Set of steel structures with anchors bolts with
corrosion-resistant coating. : Yes
Pole control cabinets with operating mechanisms
: Yes
Central (main) control cabinet : 1
Kitting list (List of all parts (main and spare) to
be included in the delivery) : Yes
SF6 (gas mixture) cylinder(s) in amount necessary
for first re-filling of the circuit-breakers up to
rated pressure : Yes
Set of CB sensors : For each pole
Installation and maintenance manual and drawings
: Yes
Certificate of conformity : Yes
Factory tests reports : Yes
Spare parts and accessories according to kitting
list,set : 1
Operational documentation, number of copies : 1
22. CB service life, years, not less than : 30
23. Mechanical withstand lifetime of cycles at C-t-O,
Class M2 as per IEC : 10000
24. Mechanical withstand lifetime at load currents of
up to 100% Ir, C-t-O, not less : 10000
10 | 150 kV Current | 1. Manufacturer: *
| Transformer | 2. Standard : IEC 61869-1, IEC61869-2 and other IEC
standards valid on the equipment manufacturing date
3. Type : Inductive, Single Phase SF6 (gas mixture)
Insulated
4. Installation : Outdoor
5. Rated Frequency, Hz : 50
6. System Nominal Voltage, kV : 150
7. Maximum Equipment volage according to IEC, kV : 170
8. Rated short-duration power- frequency
withstand voltage (RMS value), kV : 230
9. Rated lightning impulse withstand voltage
(peak- value), not less than, kV : 650
10. Rated short-circuit withstand current, kA: 40*
11. Rated peak withstand current, not less than, kA
: 100
12. Short-circuit duration time, s : 3
13. Secondary currents, A : 5
14. Primary currents ,A : 1200
15. Quantity of secondary windings:
- for Electricity metering : 1
- for measurements : 1
16. Quantity of protection cores : 4
17. Accuracy class rating of metering core : 0.2S
18. Accuracy class rating of measuring core : 0.2
19. Accuracy class rating of protection core : 10P
20. The secondary winding load, VA : *
21. The current limit factor : *
22. Min. lifetime of equipment, years : 30
23. Insulation : Polymer/ Porcelain white
or silver white*
24. Total mechanical load, not less than, N : 1500
25. Percentage of SF6 gas leaks, per year, not more
than, % : 0.5
26. Transformation ratio switch : on secondary side
Scope of supply
27. Current transformer assembly,(yes, no) : Yes
28. Operating documents (Technical passport, Test
reports, Operation and Maintenance (O&M) manual
and technical description)in English and Ukrainian
language,(yes, no) : Yes
29. Availability of contact terminals for fixing
hardware clamps (sizes to be specified),(yes, no)
: Yes
30. Cylinder(s) with SF6 gas (gas mixture) for refilling
up to rated pressure and during further
maintenance,(yes, no) : Yes
31. Certificate of compliance : Yes
32. Installation drawings with installation instruction
: Yes
33. Factory acceptance tests reports : Yes
34. Technical passport (printed document with technical
data) / Rating plate : Yes
35. SF6 density indicator, temperature-compensated,
with SF6 (gas mixture) density monitoring double-
staged signaling of the SF6 (gas mixture) density
and under pressure (warning and emergency
signaling) and auxiliary contacts,(yes, no) : Yes
11 | Circuit Breaker 750 kV | 1. Manufacturer : to be specified
2. Type : SF6 (gas mixture) 4 Interrupting chambers
3. Installation : Outdoor
4. Rated Frequency, Hz : 50
5. Operational Voltage, kV : 750
6. Rated Voltage, kV : 800
7. Rated short-circuit breaking current, not less
than, kA : 40
8. Short-time withstand current, kA, not less, kA : 40
9. Rated peak withstand current, not less than, kA
: 100
10. Short-circuit DC component time constant, ms : 45
11. Rated current, not less than, A : 4000
12. Short-circuit time, not less than, s : 3
13. Standard switching-withstand voltage (Phase-Earth
and clearance between open contacts, peak value),
not less than, kV : 1550
14. Standard switching-withstand voltage (Phase-Phase,
peak value) , not less than,kV : 2480
15. Standard lightning impulse withstand voltage (Phase
-Earth and Phase-Phase, peak value), not less than,
kV : 2100
16. Standard lightning impulse withstand voltage
(clearance between open contacts, peak value) ,
not less than, kV : 2100(+455)
17. Capacitive cut-off current, class : C2 (according
to IEC 62271-100)
18. Total breaking time, not more than, ms : 40
19. Total closing time, not more than, ms : 110
20. Delayed Automatic Reclosing Cycle
: O-0,3sec-CO-3min-CO
21. Number of switching-off events at rated current
until first maintenance, not less than, class
: M2 (according to IEC 62271-100)
22. Number of switching-off events at rated
short-circuit current until first maintenance,
for each phase not less than : 12
23. Poles breaking/ closing timediversity,
not more than, s : 0,01
24. Insulator : Porcelain, white or silver-white
25. Annual (SF6/gas mixture) Leak rate, % : ≤ 0.5
26. Temperatures change level : from -40°C to +40°C
27. Drive : for each pole
28. Type of Drive : Spring mechanism
29. Number of opening coils : 2
30. Opening coil voltage Min.-/Rated- Max. Voltage,
V DC : 154/220/242
31. Number of closing coils : 1
32. Closing coil voltage, Min.-/Rated- Max. Voltage,
V DC : 176/220/242
33. Rated voltage of the charging motor, V AC : 220
34. Number of Normal Open auxiliary contacts : 18
35. Number of Normal Close auxiliary contacts : 18
36. Voltage of heating, V AC : 220
37. Manual control by spring drive availability : Yes
38. Minimum creepage distance, cm/kV
phase-to-phase : 2,5
phase-to-earth : 4,4
39. Permissible horizontal mechanical load on HV
terminals, N, not less, N : 1500
40. Min. lifetime of equipment, years : 30
41. Mechanical withstand capability (mechanical life),
C-O operations, not less : ≥10000
42. Earthquake magnitude, MSK : 7
44. Warranty period from the date of its receipt at the
desingnated delivery place, not less than, years : 1
Scope of supply
45. Circuit-breaker with operating mechanisms, metallic
supportcolumns and anchor bolts, set : 1
46. Control cabinet, pcs : 1
47. Cylinder (cylinders) with SF6 gas (gas mixture)
for refilling up to rated pressure (yes, no): yes
48. Cables for internal connections (yes, no) : yes
49. Spare part set, according to the kitting list set,
set : 1
50. Certificate of conformity, pcs : 1
51. Certificate of origin, pcs : 1
52. Installation drawings with installation manual,
set : 1
53. Passport, pcs : 1
54. Kitting list (List of all parts (main and spare) to
be included in the delivery) : yes
55. Operational control methods and programs : yes
56. Acceptance tests reports (acts) : yes
57. Operating manuals or guidelines : yes
58. Tests control methods and programs : yes
Instruments and maintenance accessories
59. SF6 density indicator, temperature-compensated,
with SF6 (gas mixture) density monitoring
double-staged signaling of the SF6 (gas mixture)
density and underpressure (warning and emergency
signaling) and auxiliary contactsfor inhibition of
circuit-breaker operation, (yes, no) : yes
60. Mechanical indicator of Open/Close position
(yes, no) : yes
61. Control switch (local/remote) (yes, no) : yes
62. CB local control buttons (yes, no) : yes
Note: Final characteristics are defined by the design
calculations
12 | Autotransformer | 1. Technical Data of the autotransformer as per the
| single-phase | Requirements of Standard : IEC, EN, standards
| 750/330/15.75 kV 333 MVA | 2. Manufacturer of the autotransformer : *
3. Country of Origin of the autotransformer : *
4. Manufacturer designation : *
5. Transformer Type : single-phase autotransformer,
oil-filled,with OFAF cooling with undirected oil
flow,three-winding, with OLTC & OCTC, 333000kVA
rated power and voltage classes HV/MV – 750/330 kV,
for outdoor installation
Climatic Condition
6. Climatic Version and Location Category in
conformity with GOST 15150-69 : U1(for the region
with moderate climate, to be outdoor located)
7. Operating temperatures range, °С
: According to IEC 60076
Subclause 4.2, additionally: Maximum temperature
range : from -42 up to +40
8. Maximum Installation Altitude, m : Not more
than 500
9. Area's Seismic Stability of the region as per the
DSTU B V.1.1-28:2010, Points : 7
Rated Parameters and Technical Data
10. Rated Power of windings
HV, MV×А : 200/266/333
MV, MV×А : 200/266/333
LV, MV×А : 80
11. System Nominal Voltage
HV, kV : 750/√3
MV, kV : 330/√3
LV, kV : 15.75
12. Highest Voltage for Equipment (Um)
(according to IEC standard), kV
HV, kV : 800/√3
MV, kV : 362/√3
LV, kV : 17.5
14. Full Wave Lightning Impulse (LI) 750 kV winding,
kV : 2100
15. Full Wave Lightning Impulse (LI) 330 kV winding,
kV : 1175
16. Full Wave Lightning Impulse (LI) 15.75 kV winding,
kV : 125
17. Chopped Wave lightning impulse (LIC) 750 kV winding,
kV : 2310
18. Chopped Wave lightning impulse (LIC) 330 kV winding,
kV : 1290
19. Chopped Wave lightning impulse (LIC) 15.75 kV
winding, kV : 138
Switching impulse test voltage, 750 kV winding,
kV : 1675
Switching impulse test voltage, 330 kV winding,
kV : 950
Applied Voltage or line terminal AC withstand (AV)
(LTAC), 750 kV winding, not less, kV
: 750 (Phase-ground)/1100 (Phase-phase)
20. Applied Voltage or line terminal AC withstand (AV)
(LTAC) 330 kV winding, kV : 510
Neutral terminal AC withstand voltage, not less,
kV : 200
21. Applied Voltage or line terminal AC withstand (AV)
(LTAC) 15,75 kV winding, kV : 45
22. Symmetrical short-circuit current of the system
for 750 kV winding, kA : 40( seconds)
23. Symmetrical short-circuit current of the system
for 330 kV winding, kA : 50 (3 seconds)
24. Symmetrical short-circuit current of the system
for 15,75 kV winding, kA : 31,5 (3 seconds)
25. Asymmetrical short-circuit current of the system
(750 kV winding), kA : 100
26. Asymmetrical short-circuit current of the system
(330 kV winding), kA : 125
27. Asymmetrical short-circuit current of the system
(15,75 kV winding), kA : 80
28. Transformation Limit Factor
- On the Main Tap, % : ±0,5
- On the Non-Main Tap, % : ±1
29. Insulation Class of Neutral Terminal, kV : 110
30. Autotransformer neutral operation mode
: The autotransformer must be capable of operating
both in the neutral solid earthing mode, and with
the phase-shifting transformer to be connected
31. Connection Diagram and group
- for autotransformator : 1auto/1-0-0
- For three-phase bank : YNa0d11
32. Rated Frequency, Hz : 50
33. Maximum Allowable Current of Common Winding, A
: 1067
34. No Load Current (max), % : ≤0,2
35. Short-Circuit Voltage, reduced to 333 MV×A
Power at Tap Rated Voltage
HV-MV, % : 10.5 (допуск ±10%)
HV-LV, % : 30.5 (допуск ±15%)
MV-LV, % : 19.0 (допуск ±15%)
36. Short-Circuit voltage of edge taps, max./min.
HV-MV, % : 11.5/11.9 (допуск ±15%)
HV-LV, % : 30.9/30.9 (допуск ±15%)
MV-LV, % : 17.9/27.3 (допуск ±15%)
38. No Load Losses at Rated Voltage at the middle
tap-changer position, max ,kW
: ≤130 (tolerance +15% as per IEC 60076-1 provided
that the tolerance for total losses do not
exceed +10%)
Load Losses in HV-MV 333 MV×A mode at Tap Rated
Voltage at the middle tap-changer position, max, kW
- HV-MV : ≤500 (tolerance +15% as per IEC 60076-1
provided that the tolerance for total losses do
not exceed +10%)
- HV-LV : 220 (tolerance +15%)
- MV-LV : 200 (tolerance +15%)
41. Permitted temperature rise of some elements of the
autotransformers in conformity with IEC,
not more than
Top insulation liquid, ⁰С : 60
Average winding, ⁰С : 65
Hot-spot winding, ⁰С : 78
42. Resistance to short circuit currents
Thermal : in conformity with IEC
Dynamic : in conformity with IEC and shall be
demonstrated by calculation
43. Load-carrying capacity : in conformity with IEC
44. Short-term emergency overloading : in conformity
with IEC
45. Allowable voltage increases in the 50 Hz network
: in conformity with IEC
46. Partial discharge level : in conformity with IEC
47. control way and range
In-phase shifting
(by means of OLTC), % : +9.5% (20 Stages) *
-11.2%(20 Stages) *
Phase shifting (by means of the transformer,
connected to the autotransformer neutral
terminal) , kV : 68
48. Transformer Oil according to Table 4 - SOU-N EE
43-101: 2009(as amended by 13.02.2018) certified
and approved to use in Ukraine : Yes
49. Oil Preservation System : air-bag type.
50. On-Load Tap Changer (OLTC)
51. Name of Manufacturer and Country of Origin of OLTC
: To be specified
52. Type of OLTC : Vacuum switch
53. Rated through current (at maximum load), A :*
54. Rated step capacity (at maximum load) : *
When operating in a three-phase group of
autotransformers, provision in automatic and remote
control modes of simultaneous switching of
tap-changer device drives without long-term
inconsistency; blocking the operation of all drives
in case of long-term inconsistency of the drives
of tap-changer devices with the output of a signal
: Yes
Completion of the automatic control unit with a
device for manual and automatic control of the
voltage setting with the possibility of connecting
to the Substation Automation System (optical
Ethernet protocol MEK 61850): factory type of tap
changer, name and country of location of the tap
changer manufacturing plant : Yes
55. Capability of 3-type control : Yes
・local – from the drive key (buttons)
・remote –from the control board
・automatic – from the automatic control unit
56. Availability of local and remote position indicator;
signaling of the edge positions : Yes
Complete with a discrete action position sensor
: Yes
57. Quantity Counter for switching : Yes
Alarm about the prohibition of switching in case of
unacceptable overloads and temperatures of the
on-load tap-changer device : Yes
58. Availability of interlocking, - preventing from
the switching-over in case of the signal of the
OLTC overload exceeding the pre-set standard norms
: Yes
Availability of an oil temperature sensor, which
allows to block switching at contactor oil
temperatures below -25°С : Yes
Availability of alarms about the status of heaters
: Yes
59. Voltage of OLTC Power Supply
Electric Motors, V : ～400, 50 Hz (3phases+N)
Control Circuits, V : ～230, 50 Hz (1phase+N)
Signalling Circuits, V : =220
60. Mechanical endurance of OLTC with no electric load,
quantity of switching-over, at least,
thous. switching : 800
61. Electric resistance resource of the OLTC contractors
contacts, which interrupt the current in case of
switching, at least, thousand switching-overs,
thous. switching : 300
62. OLTC installed no failure operating time, at least,
thousand switching, thous. switching
: 300 prior to maintenance
63. OLTC service life (except for consumables and spare
parts), at least, Expected lifecycle when
designing.(This is NOT warranty.), Years : 30
64. OLTC switch vacuum compartment monitoring system
: the need to supply a monitoring system for the
vacuum compartment is determined by the
manufacturer of the switching device
66. OLTC: number of operations until exchange of
diverter switch unit : minimum 1.2 million
67. OLTC Monitoring : no
69. Cooling System
70. Cooling System Type: ONAN, ONAF, OFAF,
ONAN/ONAF/OFAF (Combined)
: ONAN/ONAF/OFAF (Combined: with natural air and oil
circulation / with forced air and natural oil
circulation / with forced air circulation and oil
circulation with undirected oil flow)
71. The cooling devices (radiators) design
: Flat stamped radiators
72. Coolers Arrangement : Mounted on the Tank
73. Cooling system automatics cabinet
– Automatic maintaining the temperature inside the
cabinet for normal operation in conformity with
climatic manufacture version of the
works-transformer equipment : Yes
– The cabinet protection degree not less than
IP55 : Yes
– Availability of the cabinet access monitoring
with signaling : Yes
– Current protection of the fan’s electric motors
: Yes
– Possibility of transfer to the SS control panel
of the information of the cooling system state,
including that concerning the emergency
disconnection of any working pump or fan : Yes
– Power supply of the cabinet from 2 sources
(different sections of auxiliaries’ busbars)
with automatic transfer : Yes
– cabinet lighting with an LED lamp : Yes
– hermetic cable inputs to the cabinet : Yes
74. Voltage of the Cooling System Power Supply
Electric Engines, V : ～400, 50 Hz (3phases+N)
Control Circuits, V : ～230, 50 Hz (1phase N)
Signalling Circuits, V : =200
75. Cooling system fans (except for consumables and
spare parts) service life, at least: Expected
lifecycle when designing.(This is NOT warranty.),
Years : 30
76. Combined electrical power of all cooling fans,
kW : to be specified
77. Combined electrical power of all cooling oil
pumps, kW : to be specified
Built-in Current Transformers:
78. 750 kV «А» HV Bushing:
Secondary Winding Quantity : 5
Primary current
for accounting winding, A : 1200
for relay protection winding, A : 1000-2000-3000
for measuring winding, A : 1000
Secondary current
for accounting winding, A : 5;1
for relay protection winding, A : 1
for measuring winding, A : 5
Rated Saturation Limit Factor of Relay Protection
Secondary Winding, not less : 20
Measuring Winding Devices Protection Coefficient
: 10
Winding 1 (Measuring, Account, for Monitoring
System Devices) 1200/1 A
Accuracy Class : 0.2S
Secondary Loads, VA : 15
Winding 2 (Measuring, Account, Temperature Gauge
AКM) 1200/1 A
Accuracy Class : 0,5
Secondary Loads,VA : 15
Winding 3 (Relay Protection) 1000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 4 (Relay Protection) 1000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, V×A : 30
Winding 5 (Relay Protection) 1200/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
79. 330 kV «Am» MV Bushing:
Quantity of Secondary Windings : 5
Primary Current, A
For Measuring Winding : 2000
For RP Winding : 1000-2000-3000-4000
Secondary Current, A
For Measuring Winding : 1
For RP Winding : 1
Rated Saturation Limit Factor of RP Secondary
Windings, not less : 20
Measuring Winding Devices Protection Coefficient
: 10
Winding 1 (Measuring, Account) 2000/1 A
Accuracy Class : 0.2S
Secondary Loads, VA : 15
Winding 2 (Measuring, Account) 2000/1 A
Accuracy Class : 0.5
Secondary Loads, VA : 15
Winding 3 (RP) 3000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 4 (RP) 3000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 5 (RP) 3000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
80. 15,75 kV «а» LV Bushing:
Quantity of Secondary Windings : 3
Primary Current, A : 12000
Secondary Current, A : 5
Rated Saturation Limit Factor of RP Secondary
Windings, not less : 20
Measuring Winding Devices Protection Coefficient
: 10
Winding 1 (Measuring, Account, Monitoring)
12000/5 A
Accuracy Class : 0,5
Secondary Loads, VA : 20
Winding 2 (RP) 12000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 3 (RP) 12000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
81. 15,75 kV «х» LV Bushing:
Quantity of Secondary Windings : 3
Primary Current, A : 12000
Secondary Current, A : 5
Rated Saturation Limit Factor of RP Secondary
Windings, max : 20
Winding 1 (Measuring, Account, Monitoring)
12000/5 A
Accuracy Class : 0.5
Secondary Loads, V×A : 20
Winding 2 (RP) 12000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 3 (RP) 12000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
82. Compensating Winding
Quantity of Secondary Windings : 1
Primary Current, A : 6000
Secondary Current, A : 5
Rated Saturation Limit Factor of RP Secondary
Windings, not less : 20
Winding 1 6000/5 A
Accuracy Class : 5P
Secondary Loads, VA : 30
83. 110 kV «Х» Neutral Terminal:
Quantity of Secondary Windings : 3
Primary Current, A
For Measuring Winding : 1200
For RP Winding : 2000
Secondary Current, A
For Measuring Winding : 1
For RP Winding : 5
Rated Saturation Limit Factor of RP Secondary
Windings, not less : 20
Measuring Winding Devices Protection Coefficient
: 10
Winding 1 (Measuring, Account, Monitoring) 1200/1 A
Accuracy Class : 0.5
Secondary Loads, VA : 20
Winding 2 (RP) 2000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 3 (RP) 2000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
84. Monitoring System - real-time technical condition
monitoring system of the transformer, display
and record the data : no
The transformer shall be equipped with fittings for
technological systems’signals and sensors, to
allow for connection of the condition monitoring
system in the future : Yes
Test tapping on HV bushing : yes
85. Possibility of Connection the monitoring system of
Autotransformer to PACS (Process Automatic Control
System) : Yes
Bushings
86. Type (legend), name of Manufacturer and Country
of Origin of bushings: Requirements for 750 kV
bushing insulation
: * - condenser-type bushing of hermetic
manufacture version, with oiled paper insulation
(OIP) or solid insulation (RIP) and porcelain
external insulation, for transformers, intended for
the lead-in main insulation
Insulation level according to Table 3, IEC 60137
for Highest Voltage for Equipment (Um) as below:
HV – 800 kV (Um)
: monitoring transducer to be connected,
for pollution degree “c” (IEC/TS 60815-1),
of 800 kV rated voltage, not less than 1600 A
rated current, for the outdoor located
87. Type (legend), name of Manufacturer and Country of
Origin of bushing: Requirements for 330kV, 110 kV
bushing insulation for pollution degree “c“
(IEC/TS 60815-1) Bushing 15,75 kV -pollution
degree“d” (IEC/TS 60815-1)
330 kV bushing rated voltage:362 kV
: Bushing with solid insulation of RIP type with
external porcelain or silicon insulation intended
for the lead-in main insulation monitoring
transducer to be connected, of 362 kV rated
voltage, not less than 2000 A rated current,
for the outdoor located.
110 kV bushing rated voltage:123 kV
: * - Bushing with solid insulation of RIP type
with external porcelain or silicon insulation
intended for the lead-in main insulation
monitoring transducer to be connected, of 123 kV
rated voltage, not less than 2000 A rated
current, for outdoor located
15.75 kV bushing rated voltage:17,5 kV
: * - The design version is to be specified by
the Works-Manufacturer
91. Efficient specific creepage distance of the
external insulation at the network rated voltage,
not less than (USCD, IEC 60815- 1)
For 110, 330, 750 kV bushings, cm/kV : 3,47
For 15.75 kV bushings, cm/kV : 4,33
92. HV bushing insulation monitoring
Outdoor cabinet for bushing : Yes
insulation monitoring, complete set : Yes
93. Bushing terminal clamps for connection to
flexible buses : Yes
94. Allowable loads on the contacts in the horizontal
direction, not less than:
For 750 kV and 330 kV bushings, N
: (Cantilever load testing according IEC 60137)
2500
95. Allowable loads on to the contacts in the horizontal
direction, not less than:
for 110 kV leads-in, N
: (Cantilever load testing according IEC 60137)2000
2000
750 kV bushings shall have contact clamps for
connecting three flexible 750 kV busbar wires
: Yes
Requirements to Design and Transportation
96. Tank manufacture version
: Bell-type with lower connection
Devices for disconnecting the active part in the
tank from displacement (yes, no):
- during transportation : Yes
- during operation : Yes
Earthing of active part
: outside at the bottom of the tank
98. Maintenance-free dehydrating breather : Yes
99. Gas (Buchholz) relay (main tank)
Installed on the pipe between the main tank / tap
changer and the conservator ascending towards the
conservator by 0° to 5°
Two-float design, with separate contacts providing
‘alarm’ and ‘trip’ settings.
Provision to be made for gas extraction at ground
level. : Yes
OLTC flow relay, acting to disconnect the
autotransformer in the event of an accelerated flow
of oil from the OLTC contactor tank into the oil
conservator : Yes
100. Availability of the Cooler bank shut-off valve.
Two pairs of contacts signaling the valve position
with the valve position indicator enabling visual
inspection, servicing convenience from the
stationary platform for the autotransformer : Yes
101. Availability of the valves of the pressure
dumping with the contacts for actuation signaling,
pc : 2
102. Oil level indicator in conservator and oil level
in OLTC compartment of the oil conservator.
Dial type with visual scale, providing an analogue
output for remote monitoring with two pairs of
contacts signaling the oil maximum and minimum
level : Yes
Availability of an additional oil separator in
the upper part of the tank, accessible for
maintenance from the stationary platform of
the autotransformer : Yes
Availability of thermosiphon filters
: Yes
Availability of oil and winding temperature
indicators : Yes
Availability of a fiber-optic system for measuring
the temperature of areas of dangerous overheating
of the windings : Yes
Availability of a device for monitoring the
condition of the 750, 330 and 110 kV bushings
of the autotransformer : Yes
The transformer must be equipped with signal
outputs of technological systems, as well as
sensors, for the possibility of connecting a
system for monitoring the transformer condition
in the future : Yes
Availability of a place on the lower collector of
the autotransformer cooling system for connecting
a system for monitoring the gas content in
transformer oil type HYDROCAL 1008 or equivalent
: Yes
103. Set of control cables s from the devices for
monitoring, signaling, protection, current
transformers of the autotransformer within the
auto transformer range. Power and control cables
of the cooling system to free-standing control
cabinet are to be supplied in set,providing
the control cabinet to be located at the distance
of no more than 3 m from the autotransformer
: Yes
104. Stainless steel conduit along the transformer
tank to protect the control cables to be laid
from the monitoring, signaling, protection devices,
leads-in, the current transformers to the
terminal’s cabinets, against mechanical damage
and solar radiation : Yes
105. Transformer movement : Longitudinal- Transverse
106. Roller Form : Double-flanged
107. Width of rail track
Longitudinal Movement, mm : 1524
Transverse Movement, mm : 2х1524
Distance between track axes, mm : 4164
108. Autotransformer Transportation
: With no oil, but fill with nitrogen gas
109. «Impact-indicators» on the transportation packing
for movement conditions monitoring within the
supply time period : Yes
110. Autotransformer painting colour : Light-grey
111. All control cabinets, signaling cabinets, terminal
boxes must be galvanized or manufactured of
stainless materials : Yes
Reliability Requirements
114. Service Life without Overhaul of the Main Part,
Years : 30
Note: 1. only core and coil assembly
2. Expected Lifecycle when designing.
(This is NOT warranty condition)
115. Periodicity and scope of technical servicing : *
116. Radio interference voltage, measured at 1.1
maximum operating voltage, not more than, mkV
: 2500
Safety Requirements
117. Conformity with the safety requirements,
including the fire safety requirements
: In conformity with
- GOST 12.1.004,
- GOST 12.2.007.0,
- GOST 12.2.007.2
118. Allowable values of the noise technical data, dB
: 93
Manufacturer’s Guarantees
119. Guarantee time period, Years
Warranty period for the entire supplied equipment
shall be
・from the date of its receipt at the designated
delivery place. : 1
120. Technical support (servicing) in Ukraine
: Yes (based on separate agreement)
(to be discussed and agreed between Ukrenergo
and the contractor)
121. Complete Set of Supply : Yes
122. Single-Phase Autotransformer, in conformity with
the Complete Set Data Sheet
: 3 x Single Phase unit
123. Nitrogen Gas or Dry Air: Transportation to site,
during temporary storage at site and for replenish
: Yes
Transformer oil: In the amount required for
complete filling-in : Yes
for process operations and replenishing during
installation works : 10% of the amount of complete
filling-in
Silica gel in the amount necessary for
commissioning of the autotransformer : Yes
124. Fire-fighting system to be used in cases of inner
damages (SERGI France) : no
125. Automatics cabinet for the cooling system : Yes
Device for monitoring the condition of 750,
330 kV bushings of autotransformer : Yes
126. Power and control cables with copper cores with
retardant insulation to be used for connection of
the current transformers, control and signaling
devices; screened cables with retardant insulation
for connection of the gauges with analogous signal
of Pt100, 4…20 mА… type; which are to be laid
within the autotransformer range in stainless
steel hoses of diameters,mm2:
- From current transformers : 2.5
- From monitoring devices : 1.5
Structures on the autotransformer tank for laying
power and control cables : Yes
A set of spare parts with a mandatory supply of a
backup safety membrane of the OLTC contactor : Yes
127. Supply technical support (condition and
completeness accepting together with manufacturer
and Supplier, installation supervision)
: Yes, in the absence of force majeure
circumstances on the territory of Ukraine (in
case safety level is less or equal 2 by Ministry
of Foreign Affairs in Japan)
Documentation (in Ukrainian) to be submitted
: English; all documents
Ukrainian; Technical Specification, Installation
& O&M manual, Factory Acceptance Tests Reports
(Certificates)
128. Complete Set Data Sheet : Yes
129. Quality Certificate : Yes
130. Origin Certificate : Yes
131. Certificates for autotransformer and completing
parts (products) of the system : Yes
Instructions for transportation, unloading,
storage, installation and commissioning of the
autotransformer : Yes
Dimensional and installation drawings of the AT,
control cabinet diagrams (electrical principle
diagram, diagram of electrical connections,
installation of control cables), diagrams of the
drive and OLTC regulator : Yes
132. Technical Description and Operation Manuals or
Operation Guidelines (which include the
documentation for planned repair) for the
autotransformer, completing parts and systems
: Yes
133. Control Diagrams of the Cooling Systems and OLTC
: Yes
Test programs and methods of control
: Yes
134. Transfer-Acceptance Tests Protocols (Certificates)
: Yes
Shall submit Factory Acceptance Test Reports.
Further Type Test as per IEC Standards excluding
Short Circuit Test shall conducted on 1st
Transformer. Calculations towards Short Circuit
shall be submitted during detailed engineering.
*- The parameters are to be determined by the
transformer manufacturer
Total price of the Equipment
Packing/Transportation price
Insurance
Grand Total