## 機材仕様明細書 (清書)
機材仕様明細書
調達番号 | 機 材 名 | 仕 様 | 数量 | 単位
0 | 総則 | 1. 中古品は認めない。
２．下記の仕様を満たし、空送が可能であり、別途指定する納入期限内に納入できる
本邦メーカーの銘柄であれば、見積先以外の本邦代替銘柄の提案も可能とする。
代替銘柄の提案は質問回答のメールにて行い、カタログ等仕様がわかるものを添付する
３. 電源を必要とする機材については、仕様欄に記載の有無に かかわらず、
機材を正常に作動させるために必要とされる資機材（電源ｹｰﾌﾞﾙ、変換ﾌﾟﾗｸﾞ、
電圧変換器など）は、当該機材に含めること。
４．電源を必要とする機材は、浄水装置側のアクセサリーにCタイプのアダプタを含め、
アダプタ使用時における作動も保証対象の範囲とすること。納入機材の電源ﾌﾟﾗｸﾞが
指定のﾀｲﾌﾟに出来ない場合は、変換ﾌﾟﾗｸﾞの使用を認める。
もしくは電源の取り出し方法を説明すること。
５．銘板、取扱説明書の記載は英語又はウクライナ語とする。
６．ﾒｰｶｰ設定の標準付属品は、仕様欄に記載がなくとも当該機材の付属品として
含めること。
７．機材を設置し、同機材が正常に作動するために必要な資機材（据え付け部材、
電源ｹｰﾌﾞﾙ、ﾄﾗﾝｽなど）は、仕様欄に記載がなくとも当該機材に含めること。
８．各機、5,500時間稼働分のスペアパーツを含めること。
９．0℃程度でも耐久性のある仕様であること。
１０．本機材調達契約受注時に受注者は発注者へ各銘柄のSDSもしくはSDSに
相当する内容を示した書類を提出すること。
１１．各機材の３辺の各々の最大の長さは以下詳細仕様に記載のDimentionの通りとする。
1 | Water Purification Equipment | Common Specifications | 7 | 台
| Reference model: | 1．General Description
| MIYASAKA Industries Co.,LTD | (1) The product shall be suitable for generating drinkable water.
| NOMERUZO BIG1-RO | 2. Specification
(1) Capabilities
8.0 ton/Day or more
(2) Dimension
560mm x 760mm x 1420mm
(3) Weight
100kg or less
(4) Type
Reverse Osmosis membrane
(5) Power Source
Electric (AC100V/1000W or less)
3. Standard accessories
Step down transformer 220/100V (1pc/unit) Instruction manual (English) (1pc/unit) Special tools (1set/unit)
4. Consumables
Pre-filter (for 5,500 hours operation) Carbon filter (for 5,500 hours operation) RO membrane filter (for 5,500 hours operation)
2 | Water Purification Equipment | Common Specifications | 5 | 台
| Reference model: | 1．General Description
| Nippon Basic Co., Ltd. | (1) The product shall be suitable for generating drinkable water.
| Cycloclean 1500 | 2. Specification
(1) Capabilities
35 ton/Day or more
(2) Dimension
650mm x 900mm x 700mm
(3) Weight
60kg or less
(4) Type
Hollow Fiber Membrane
(5) Power Source
Gasoline Engine, Manual
3. Standard accessories
Hose for purified water (A-hose) (1pc/unit) Feed water hose with a strainer (B-hose) (1pc/unit) Hose band (2pcs/unit) Filter housing wrench (1pc/unit) Instruction manual (English) (1pc/unit)
4. Consumables
250mm 1µ pre-filter (for 5,500 hours operation) 250mm Hybrid Carbon Filter (for 5,500 hours operation) 250mm MF Hollow Fiber Membrane Filter (for 5,500 hours operation)
3 | Water Purification Equipment | Common Specifications | 28 | 台
| Reference model: | 1．General Description
| Nippon Basic Co., Ltd. | (1) The product shall be suitable for generating drinkable water.
| Cycloclean portable SPX | 2. Specification
(1) Capabilities
2.4 ton/Day or more
(2) Dimension
600mm x 400mm x 300mm
(3) Weight
15kg or less
(4) Type
Hollow Fiber Membrane
(5) Power Source
Electric (AC220V/50W or less)
3. Standard accessories
Water resources hose with strainer (4m) (1pc/unit) Pure water hose (0.5m) (1pc/unit) Joint hose (1m) (1pc/unit) 10 liters water tank (1pc/unit) Instruction manual (English) (1pc/unit)
4. Consumables
Three-layer filter USJ-2007-01 (for 5,500 hours operation)
4 | Water Purification Equipment | Common Specifications | 4 | 台
| Reference model: | 1．General Description
| Kansuikoubou Co., Ltd | (1) The product shall be suitable for generating drinkable water.
| Manual RO filtration system | 2. Specification
| (Including in-water pump 4 sets) | (1) Capabilities
43.2 ton/Day or more
(2) Dimension
1700mm x 950mm x 1100mm
(3) Weight
150kg or less
(4) Type
Reverse Osmosis Membrane
(5) Power Source
Electric (AC 200V)
3. Standard accessories
Instruction manual in book (English or Ukrainian, 1pc/unit)
Instruction manual in USB or DVD (English or Ukrainian, 1pc/unit)
4. Consumables
RO membrane filter (for 5,500 hours operation)
UF membrane filter (for 5,500 hours operation)
5 | Water Purification Equipment | Common Specifications | 1 | 台
| Reference model: | 1．General Description
| Kansuikoubou Co., Ltd | (1) The product shall be suitable for generating drinkable water.
| Manual UF filtration system | 2. Specification
(1) Capabilities
25 ton/Day or more
(2) Dimension
1700mm x 900mm x 800mm
(3) Weight
130kg or less
(4) Type
Ultrafiltration Membrane
(5) Power Source
Electric (AC 200V)
3. Standard accessories
Instruction manual in book (English or Ukrainian, 1pc/unit)
Instruction manual in USB or DVD (English or Ukrainian, 1pc/unit)
4. Consumables
UF membrane filter (for 5,500 hours operation)
6 | Water Purification Equipment | Common Specifications | 1 | 台
| Reference model: | 1．General Description
| Kansuikoubou Co., Ltd | (1) The product shall be suitable for generating drinkable water.
| Manual UF filtration system | 2. Specification
(1) Capabilities
50 ton/Day or more
(2) Dimension
1100mm x 700mm x 1900mm
(3) Weight
130kg or less
(4) Type
Ultrafiltration Membrane
(5) Power Source
Electric (AC 200V)
3. Standard accessories
Instruction manual in book (English or Ukrainian, 1pc/unit)
Instruction manual in USB or DVD (English or Ukrainian, 1pc/unit)
7 | Water Purification Equipment | Common Specifications | 1 | 台
| Reference model: | 1．General Description
| Kansuikoubou Co., Ltd | (1) The product shall be suitable for generating drinkable water.
| Manual IM filtration system | 2. Specification
(1) Capabilities
25 ton/Day or more
(2) Dimension
1600mm x 600mm x1200mm
(3) Weight
110kg or less
(4) Type
Immerse Membrane
(5) Power Source
Electric (AC 200V)
3. Standard accessories
Instruction manual in book (English or Ukrainian, 1pc/unit)
Instruction manual in USB or DVD (English or Ukrainian, 1pc/unit)
4. Consumables
UF membrane filter (for 5,500 hours operation)
8 | Water Purification Equipment | Common Specifications | 3 | 台
| Reference model: | 1．General Description
| Kansuikoubou Co., Ltd | (1) The product shall be suitable for generating drinkable water.
| Manual In-tank IM filtration system | 2. Specification
| (Including Pump) | (1) Capabilities
25 ton/Day or more
(2) Dimension
1050mm x 350mm x 350mm
(3) Weight
40kg or less
(4) Type
Immerse Membrane
(5) Power Source
Electric (AC 200V)
3. Standard accessories
Instructionmanual in book (English or Ukrainian, 1pc/unit)
Instructionmanual in USB or DVD (English or Ukrainian, 1pc/unit)
4. Consumables
UF membrane filter (for 5,500 hours operation)
9 | Water Purification Equipment | Common Specifications | 1 | 台
| Reference model: | 1．General Description
| Kansuikoubou Co., Ltd | (1) The product shall be suitable for generating drinkable water.
| Manual UF filtration system | 2. Specification
(1) Capabilities
25 ton/Day or more
(2) Dimension
1850mm x 550mm x 1100mm
(3) Weight
150kg or less
(4) Type
Ultrafiltration Membrane
(5) Power Source
Electric (AC 200V)
3. Standard accessories
Instruction manual in book (English or Ukrainian, 1pc/unit)
Instruction manual in USB or DVD (English or Ukrainian, 1pc/unit)
4. Consumables
UF membrane filter (for 5,500 hours operation)
10 | Water Purification Equipment | Common Specifications | 1 | 台
| Reference model: | 1．General Description
| OH Charge Laboratory Co,.LTD | (1) The product shall be suitable for generating drinkable water.
| DW-300T | 2. Specification
(1) Capabilities
70 ton/Day or more
(2) Dimension
1500mm x 600mm x 1200mm
(3) Weight
160kg or less
(4) Type
Ceramic Filter
(5) Power Source
Electric (AC220V/1100W or less)
3. Standard accessories
Step down transformer 220/100V (1pc/unit)
Instruction manual (English) (1pc/unit)
4. Consumables
Ceramic filter (for 5,500 hours operation)
11 | Water Purification Equipment | Common Specifications | 1 | 台
| Reference model: | 1．General Description
| OH Charge Laboratory Co,.LTD | (1) The product shall be suitable for generating drinkable water.
| AT-WK50-L | 2. Specification
(1) Capabilities
70 ton/Day or more
(2) Dimension
1000mm x 1100mm x 2000mm
(3) Weight
550kg or less
(4) Type
Ceramic Filter
(5) Power Source
Electric (AC220-230V, 0.5kW)
3. Standard accessories
Instruction manual (English) (1pc/unit)
4. Consumables
Ceramic filter (for 5,500 hours operation) Bags of salt (25 kg/bag) (for 5,500 hours operation)
12 | Water Purification Equipment | Common Specifications | 1 | 台
| Reference model: | 1．General Description
| JFE Engineering Co,.LTD | (1) The product shall be suitable for generating drinkable water.
| Water Purification Unit type 2 | 2. Specification
(1) Capabilities
40 ton/Day or more
(2) Dimension
1900mm x 700mm x 1700mm
(3) Weight
260kg or less
(4) Type
Microfiltration Membrane
(5) Power Source
Electric (AC100V, 2600VA or less)
3. Standard accessories
Instruction manual (English) (1pc/unit)
4. Consumables
Pre-filters (Length:500mm, Nominal hole diameter: 100µm, Filter material: PP) (for 5,500 hours operation) Activated carbon filters (Length: 250mm, Filter material: activated carbon fiber) (for 5,500 hours operation) MF membrane modules (MF membrane=nominal diameter 0.1µm, membrane area: 23m2, membrane material: PVDF, case material: ABS) (for 5,500 hours operation)
13 | Water Purification Equipment | Common Specifications | 1 | 台
| Reference model: | 1．General Description
| JFE Engineering Co,.LTD | (1) The product shall be suitable for generating drinkable water.
| Water Purification Unit type MIZUHIME | 2. Specification
(1) Capabilities
5 ton/Day or more
(2) Dimension
800mm x 600mm x 700mm
(3) Weight
40kg or less
(4) Type
Hollow Fiber Membrane
(5) Power Source
Electric (AC100V, 500VA or less)
3. Standard accessories
Instruction manual (English) (1pc/unit)
4. Consumables
Pre-filters (Length:2500mm, Nominal hole diameter: 100µm) (for 5,500 hours operation) Activated carbon filters (Length: 250mm, Filter material: activated carbon fiber) (for 5,500 hours operation) Hollow fiber membranes (Hollow fiber membrane: hole diameter 0.05 to 0.1µm, membrane area: 0.5m2) (for 5,500 hours operation)