## Sheet1
Technical Specifications
Item No. | Name of Equipment | Description (Required by Employer) | Proposed by Competitor | Note
(e.g.) | Surge Arrester ●● kV | 1. General technical descriptions
1.1 Standard : IEC 600●●-●:●
1.2 Manufacturer : *
1.3 Conditional denotation (brand) : *
1.4 Rated voltage, kV : ●●
1.5 Maximum operating system voltage, kV : ●●
1.6 SA rated voltage, kV, not less: ●●
| Common Requirements | Following documents shall be submitted and approved by
Ukrenergo.
1. Outline drawing for the equipment
2. Schematic diagram (if applicable)
3. Tehcnical specification
4. Operation & Maintenance manual
5. Packing list
6. Factory test plan
7. Factory test report
The above item 4.6. and 7. shall be translated into Ukraine
language but the English documents to be referred as official
documents. Other documents, including name plate, shall be
provided in English only.
Witness by Ukrenergo will not be required for the factory test.
12 | Autotransformer | 1. Technical Data of the autotransformer as per the
| single-phase | Requirements of Standard : IEC, EN, standards
| 750/330/15.75 kV 333 MVA | 2. Manufacturer of the autotransformer : *
| 3 phases | 3. Country of Origin of the autotransformer : *
4. Manufacturer designation : *
5. Transformer Type : single-phase autotransformer,
oil-filled,with OFAF cooling with undirected oil
flow,three-winding, with OLTC & OCTC, 333000kVA
rated power and voltage classes HV/MV – 750/330 kV,
for outdoor installation
Climatic Condition
6. Climatic Version and Location Category in
conformity with GOST 15150-69 or IEC equivalent : U1(for the
region with moderate climate, to be outdoor located)
7. Operating temperatures range, °С
: According to IEC 60076
Subclause 4.2, additionally: Maximum temperature
range : from -42 up to +40
8. Maximum Installation Altitude, m : Not more
than 500
9. Area's Seismic Stability of the region as per the
DSTU B V.1.1-28:2010, Points : 7
Rated Parameters and Technical Data
10. Rated Power of windings
HV, MV×А : 200/266/333
MV, MV×А : 200/266/333
LV, MV×А : 80
11. System Nominal Voltage
HV, kV : 750/√3
MV, kV : 330/√3
LV, kV : 15.75
12. Highest Voltage for Equipment (Um)
(according to IEC standard), kV
HV, kV : 800/√3
MV, kV : 362/√3
LV, kV : 17.5
14. Full Wave Lightning Impulse (LI) 750 kV winding,
kV : 2100
15. Full Wave Lightning Impulse (LI) 330 kV winding,
kV : 1175
16. Full Wave Lightning Impulse (LI) 15.75 kV winding,
kV : 125
17. Chopped Wave lightning impulse (LIC) 750 kV winding,
kV : 2310
18. Chopped Wave lightning impulse (LIC) 330 kV winding,
kV : 1290
19. Chopped Wave lightning impulse (LIC) 15.75 kV
winding, kV : 138
Switching impulse test voltage, 750 kV winding,
kV : 1675
Switching impulse test voltage, 330 kV winding,
kV : 950
Applied Voltage or line terminal AC withstand (AV)
(LTAC), 750 kV winding, not less, kV
: 750 (Phase-ground)/1100 (Phase-phase)
20. Applied Voltage or line terminal AC withstand (AV)
(LTAC) 330 kV winding, kV : 510
Neutral terminal AC withstand voltage, not less,
kV : 200
21. Applied Voltage or line terminal AC withstand (AV)
(LTAC) 15,75 kV winding, kV : 45
22. Symmetrical short-circuit current of the system
for 750 kV winding, kA : 40(3 seconds)
23. Symmetrical short-circuit current of the system
for 330 kV winding, kA : 50 (3 seconds)
24. Symmetrical short-circuit current of the system
for 15,75 kV winding, kA : 31,5 (3 seconds)
25. Asymmetrical short-circuit current of the system
(750 kV winding), kA : 100
26. Asymmetrical short-circuit current of the system
(330 kV winding), kA : 125
27. Asymmetrical short-circuit current of the system
(15,75 kV winding), kA : 80
28. Transformation Limit Factor
- On the Main Tap, % : ±0,5
- On the Non-Main Tap, % : ±1
29. Insulation Class of Neutral Terminal, kV : 110
30. Autotransformer neutral operation mode
: The autotransformer must be capable of operating
both in the neutral solid earthing mode, and with
the phase-shifting transformer to be connected
31. Connection Diagram and group
- for autotransformator : 1auto/1-0-0
- For three-phase bank : YNa0d11
32. Rated Frequency, Hz : 50
33. Maximum Allowable Current of Common Winding, A
: 1067
34. No Load Current (max), % : ≤0,2
35. Short-Circuit Voltage, reduced to 333 MVA
Power at Tap Rated Voltage
HV-MV, % : 10.5 (tolerance ±10%)
HV-LV, % : 30.5 (tolerance ±15%)
MV-LV, % : 19.0 (tolerance ±15%)
36. Short-Circuit voltage of edge taps, max./min.
HV-MV, % : 11.5/11.9 (tolerance ±15%)
HV-LV, % : 30.9/30.9 (tolerance ±15%)
MV-LV, % : 17.9/27.3 (tolerance ±15%)
38. No Load Losses at Rated Voltage at the middle
tap-changer position, max ,kW
: ≤130 (tolerance +15% as per IEC 60076-1 provided
that the tolerance for total losses do not
exceed +10%)
Load Losses in HV-MV 333 MV×A mode at Tap Rated
Voltage at the middle tap-changer position, max, kW
- HV-MV : ≤500 (tolerance +15% as per IEC 60076-1
provided that the tolerance for total losses do
not exceed +10%)
- HV-LV : 220 (tolerance +15%)
- MV-LV : 200 (tolerance +15%)
41. Permitted temperature rise of some elements of the
autotransformers in conformity with IEC,
not more than
Top insulation liquid, ⁰С : 60
Average winding, ⁰С : 65
Hot-spot winding, ⁰С : 78
42. Resistance to short circuit currents
Thermal : in conformity with IEC
Dynamic : in conformity with IEC and shall be
demonstrated by calculation
43. Load-carrying capacity : in conformity with IEC
44. Short-term emergency overloading : in conformity
with IEC
45. Allowable voltage increases in the 50 Hz network
: in conformity with IEC
46. Partial discharge level : in conformity with IEC
47. control way and range
In-phase shifting
(by means of OLTC), % : +9.5% (20 Stages) *
-11.2%(20 Stages) *
Phase shifting (by means of the transformer,
connected to the autotransformer neutral
terminal) , kV : 68
48. Transformer Oil according to Table 4 - SOU-N EE
43-101: 2009(as amended by 13.02.2018) certified and approved
to use in Ukraine,namely: Nytro 11 GX, Nytro 10 XN, Nytro Lyra X,
HyVolt III, Shell Diala S4 ZX-I, T-1500 (Azerbaijan) : Yes
49. Oil Preservation System : air-bag type.
50. On-Load Tap Changer (OLTC)
51. Name of Manufacturer and Country of Origin of OLTC
: To be specified
52. Type of OLTC : Vacuum switch
53. Rated through current (at maximum load), A :*
54. Rated step capacity (at maximum load) : *
When operating in a three-phase group of
autotransformers, provision in automatic and remote
control modes of simultaneous switching of
tap-changer device drives without long-term
inconsistency; blocking the operation of all drives
in case of long-term inconsistency of the drives
of tap-changer devices with the output of a signal
: Yes
Completion of the automatic control unit with a
device for manual and automatic control of the
voltage setting with the possibility of connecting
to the Substation Automation System (optical
Ethernet protocol MEK 61850): factory type of tap
changer, name and country of location of the tap
changer manufacturing plant : Yes
55. Capability of 3-type control : Yes
・local – from the drive key (buttons)
・remote –from the control board
・automatic – from the automatic control unit
56. Availability of local and remote position indicator;
signaling of the edge positions : Yes
Complete with a discrete action position sensor
: Yes
57. Quantity Counter for switching : Yes
Alarm about the prohibition of switching in case of
unacceptable overloads and temperatures of the
on-load tap-changer device : Yes
58. Availability of interlocking, - preventing from
the switching-over in case of the signal of the
OLTC overload exceeding the pre-set standard norms
: Yes
Availability of an oil temperature sensor, which
allows to block switching at contactor oil
temperatures below -25°С : Yes
Availability of alarms about the status of heaters
: Yes
59. Voltage of OLTC Power Supply
Electric Motors, V : ～400, 50 Hz (3phases+N)
Control Circuits, V : ～230, 50 Hz (1phase+N)
Signalling Circuits, V : =220
60. Mechanical endurance of OLTC with no electric load,
quantity of switching-over, at least,
thous. thousands switching : 800
61. Electric resistance resource of the OLTC contractors
contacts, which interrupt the current in case of
switching, at least, thousand switching-overs,
thous. thousands switching : 300
62. OLTC installed no failure operating time, at least,
thousand switching, thous.thousands switching
: 300 prior to maintenance
63. OLTC service life (except for consumables and spare
parts), at least, Expected lifecycle when
designing.(This is NOT warranty.), Years : 30
64. OLTC switch vacuum compartment monitoring system
: the need to supply a monitoring system for the
vacuum compartment is determined by the
manufacturer of the switching device
66. OLTC: number of operations until exchange of
diverter switch unit : minimum 1.2 million
67. OLTC Monitoring : no
69. Cooling System
70. Cooling System Type: ONAN, ONAF, OFAF,
ONAN/ONAF/OFAF (Combined)
: ONAN/ONAF/OFAF (Combined: with natural air and oil
circulation / with forced air and natural oil
circulation / with forced air circulation and oil
circulation with undirected oil flow)
71. The cooling devices (radiators) design
: Flat stamped radiators
72. Coolers Arrangement : Mounted on the Tank
73. Cooling system automatics cabinet
– Automatic maintaining the temperature inside the
cabinet for normal operation in conformity with
climatic manufacture version of the
works-transformer equipment : Yes
– The cabinet protection degree not less than
IP55 : Yes
– Availability of the cabinet access monitoring
with signaling : Yes
– Current protection of the fan’s electric motors
: Yes
– Possibility of transfer to the SS control panel
of the information of the cooling system state,
including that concerning the emergency
disconnection of any working pump or fan : Yes
– Power supply of the cabinet from 2 sources
(different sections of auxiliaries’ busbars)
with automatic transfer : Yes
– cabinet lighting with an LED lamp : Yes
– hermetic cable inputs to the cabinet : Yes
74. Voltage of the Cooling System Power Supply
Electric Engines, V : ～400, 50 Hz (3phases+N)
Control Circuits, V : ～230, 50 Hz (1phase N)
Signalling Circuits, V : = 220
75. Cooling system fans (except for consumables and
spare parts) service life, at least: Expected
lifecycle when designing.(This is NOT warranty.),
Years : 30
76. Combined electrical power of all cooling fans,
kW : to be specified
77. Combined electrical power of all cooling oil
pumps, kW : to be specified
Built-in Current Transformers:
78. 750 kV «А» HV Bushing:
Secondary Winding Quantity : 5
Primary current
for accounting winding, A : 1200
for relay protection winding, A : 1000-2000-3000
for measuring winding, A : 1000
Secondary current
for accounting winding, A : 5;1
for relay protection winding, A : 1
for measuring winding, A : 5
Rated Saturation Limit Factor of Relay Protection
Secondary Winding, not less : 20
Measuring Winding Devices Protection Coefficient
: 10
Winding 1 (Measuring, Account, for Monitoring
System Devices) 1200/1 A
Accuracy Class : 0.2S
Secondary Loads, VA : 15
Winding 2 (Measuring, Account, Temperature Gauge
AКM) 1200/1 A
Accuracy Class : 0,5
Secondary Loads,VA : 15
Winding 3 (Relay Protection) 1000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 4 (Relay Protection) 1000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, V×A : 30
Winding 5 (Relay Protection) 1200/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
79. 330 kV «Am» MV Bushing:
Quantity of Secondary Windings : 5
Primary Current, A
For Measuring Winding : 2000
For RP Winding : 1000-2000-3000-4000
Secondary Current, A
For Measuring Winding : 1
For RP Winding : 1
Rated Saturation Limit Factor of RP Secondary
Windings, not less : 20
Measuring Winding Devices Protection Coefficient
: 10
Winding 1 (Measuring, Account) 2000/1 A
Accuracy Class : 0.2S
Secondary Loads, VA : 15
Winding 2 (Measuring, Account) 2000/1 A
Accuracy Class : 0.5
Secondary Loads, VA : 15
Winding 3 (RP) 3000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 4 (RP) 3000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 5 (RP) 3000-2000/1 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
80. 15,75 kV «а» LV Bushing:
Quantity of Secondary Windings : 3
Primary Current, A : 12000
Secondary Current, A : 5
Rated Saturation Limit Factor of RP Secondary
Windings, not less : 20
Measuring Winding Devices Protection Coefficient
: 10
Winding 1 (Measuring, Account, Monitoring)
12000/5 A
Accuracy Class : 0,5
Secondary Loads, VA : 20
Winding 2 (RP) 12000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 3 (RP) 12000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
81. 15,75 kV «х» LV Bushing:
Quantity of Secondary Windings : 3
Primary Current, A : 12000
Secondary Current, A : 5
Rated Saturation Limit Factor of RP Secondary
Windings, max : 20
Winding 1 (Measuring, Account, Monitoring)
12000/5 A
Accuracy Class : 0.5
Secondary Loads, V×A : 20
Winding 2 (RP) 12000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 3 (RP) 12000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
82. Compensating Winding
Quantity of Secondary Windings : 1
Primary Current, A : 6000
Secondary Current, A : 5
Rated Saturation Limit Factor of RP Secondary
Windings, not less : 20
Winding 1 6000/5 A
Accuracy Class : 5P
Secondary Loads, VA : 30
83. 110 kV «Х» Neutral Terminal:
Quantity of Secondary Windings : 3
Primary Current, A
For Measuring Winding : 1200
For RP Winding : 2000
Secondary Current, A
For Measuring Winding : 1
For RP Winding : 5
Rated Saturation Limit Factor of RP Secondary
Windings, not less : 20
Measuring Winding Devices Protection Coefficient
: 10
Winding 1 (Measuring, Account, Monitoring) 1200/1 A
Accuracy Class : 0.5
Secondary Loads, VA : 20
Winding 2 (RP) 2000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
Winding 3 (RP) 2000/5 A
Accuracy Class : 5P20
Secondary Loads, VA : 30
84. Monitoring System - real-time technical condition
monitoring system of the transformer, display
and record the data : no
The transformer shall be equipped with fittings for
technological systems’signals and sensors, to
allow for connection of the condition monitoring
system in the future : Yes
Test tapping on HV bushing : yes
85. Possibility of Connection the monitoring system of
Autotransformer to PACS (Process Automatic Control
System) : Yes
Bushings
86. Type (legend), name of Manufacturer and Country
of Origin of bushings: Requirements for 750 kV
bushing insulation
: * - condenser-type bushing of hermetic
manufacture version, with oiled paper insulation
(OIP) or solid insulation (RIP) and porcelain
external insulation, for transformers, intended for
the lead-in main insulation
Insulation level according to Table 3, IEC 60137
for Highest Voltage for Equipment (Um) as below:
HV – 800 kV (Um)
: monitoring transducer to be connected,
for pollution degree “c” (IEC/TS 60815-1),
of 800 kV rated voltage, not less than 1600 A
rated current, for the outdoor located
87. Type (legend), name of Manufacturer and Country of
Origin of bushing: Requirements for 330kV, 110 kV
bushing insulation for pollution degree “c“
(IEC/TS 60815-1) Bushing 15,75 kV -pollution
degree“d” (IEC/TS 60815-1)
330 kV bushing rated voltage, not less:362 kV
: Bushing with solid insulation of RIP type with
external porcelain or silicon insulation intended
for the lead-in main insulation monitoring
transducer to be connected, of 362 kV rated
voltage, not less than 2000 A rated current,
for the outdoor located.
110 kV bushing rated voltage, not less:123 kV
: * - Bushing with solid insulation of RIP type
with external porcelain or silicon insulation
intended for the lead-in main insulation
monitoring transducer to be connected, of not less than 123 kV
rated voltage, not less than 2000 A rated
current, for outdoor located
15.75 kV bushing rated voltage, not less :17.5 kV
: * - The design version is to be specified by
the Works-Manufacturer
91. Efficient specific creepage distance of the
external insulation at the network rated voltage,
not less than (USCD, IEC 60815- 1)
For 110, 330, 750 kV bushings, cm/kV : 3,47
For 15.75 kV bushings, cm/kV : 4,33
92. HV bushing insulation monitoring
Outdoor cabinet for bushing : Yes
insulation monitoring, complete set : Yes
93. Bushing terminal clamps for connection to
flexible buses : Yes
94. Allowable loads on the contacts in the horizontal
direction, not less than:
For 750 kV and 330 kV bushings, N
: (Cantilever load testing according IEC 60137)
2500
95. Allowable loads on to the contacts in the horizontal
direction, not less than:
for 110 kV leads-in, N
: (Cantilever load testing according IEC 60137)2000
2000
750 kV bushings shall have contact clamps for
connecting three flexible 750 kV busbar wires
: Yes
Requirements to Design and Transportation
96. Tank manufacture version
: Bell-type with lower connection
Devices for disconnecting the active part in the
tank from displacement (yes, no):
- during transportation : Yes
- during operation : Yes
Earthing of active part
: outside at the bottom of the tank
98. Maintenance-free dehydrating breather : Yes
99. Gas (Buchholz) relay (main tank)
Installed on the pipe between the main tank / tap
changer and the conservator ascending towards the
conservator by 0° to 5°
Two-float design, with separate contacts providing
‘alarm’ and ‘trip’ settings.
Provision to be made for gas extraction at ground
level. : Yes
OLTC flow relay, acting to disconnect the
autotransformer in the event of an accelerated flow
of oil from the OLTC contactor tank into the oil
conservator : Yes
100. Availability of the Cooler bank shut-off valve.
Two pairs of contacts signaling the valve position
with the valve position indicator enabling visual
inspection, servicing convenience from the
stationary platform for the autotransformer : Yes
101. Availability of the valves of the pressure
dumping with the contacts for actuation signaling,
pc : 2
102. Oil level indicator in conservator and oil level
in OLTC compartment of the oil conservator.
Dial type with visual scale, providing an analogue
output for remote monitoring with two pairs of
contacts signaling the oil maximum and minimum
level : Yes
Availability of an additional oil separator in
the upper part of the tank, accessible for
maintenance from the stationary platform of
the autotransformer : Yes
Availability of thermosiphon filters
: Yes
Availability of oil and winding temperature
indicators : Yes
Availability of a fiber-optic system for measuring
the temperature of areas of dangerous overheating
of the windings : Yes
Availability of a device for monitoring the
condition of the 750, 330 and 110 kV bushings
of the autotransformer : Yes
The transformer must be equipped with signal
outputs of technological systems, as well as
sensors, for the possibility of connecting a
system for monitoring the transformer condition
in the future : Yes
Availability of a place on the lower collector of
the autotransformer cooling system for connecting
a system for monitoring the gas content in
transformer oil type HYDROCAL 1008 or equivalent
: Yes
103. Set of control cables s from the devices for
monitoring, signaling, protection, current
transformers of the autotransformer within the
auto transformer range. Power and control cables
of the cooling system to free-standing control
cabinet are to be supplied in set,providing
the control cabinet to be located at the distance
of no more than 3 m from the autotransformer
: Yes
104. Stainless steel conduit along the transformer
tank to protect the control cables to be laid
from the monitoring, signaling, protection devices,
leads-in, the current transformers to the
terminal’s cabinets, against mechanical damage
and solar radiation : Yes
105. Transformer movement : Longitudinal- Transverse
106. Roller Form : Double-flanged
107. Width of rail track
Longitudinal Movement, mm : 1524
Transverse Movement, mm : 2х1524
Distance between track axes, mm : 4164
108. Autotransformer Transportation
: With no oil, but fill with nitrogen gas or Dry Air
109. «Impact-indicators» on the transportation packing
for movement conditions monitoring within the
supply time period : Yes
110. Autotransformer painting colour : Light-grey
111. All control cabinets, signaling cabinets, terminal
boxes must be galvanized or manufactured of
stainless materials : Yes
Reliability Requirements
114. Service Life without Overhaul of the Main Part,
Years : 30
Note: 1. only core and coil assembly
2. Expected Lifecycle when designing.
(This is NOT warranty condition)
115. Periodicity and scope of technical servicing : *
116. Radio interference voltage, measured at 1.1
maximum operating voltage, not more than, mkV
: 2500
Safety Requirements
117. Conformity with the safety requirements,
including the fire safety requirements
: In conformity with followings or IEC equivalent
- GOST 12.1.004,
- GOST 12.2.007.0,
- GOST 12.2.007.2
118. Allowable values of the noise technical data, dB
: 93
Manufacturer’s Guarantees
119. Guarantee time period, Years
Warranty period for the entire supplied equipment
shall be
・from the date of its receipt at the designated
delivery place. : 1
120. Technical support (servicing) in Ukraine
: Yes (based on separate agreement)
(to be discussed and agreed between Ukrenergo
and the contractor)
121. Complete Set of Supply : Yes
122. Single-Phase Autotransformer, in conformity with
the Complete Set Data Sheet
: 3 x Single Phase unit
123. Nitrogen Gas or Dry Air: Transportation to site,
during temporary storage at site and for replenish
: Yes
Transformer oil: In the amount required for
complete filling-in : Yes
for process operations and replenishing during
installation works : 10% of the amount of complete
filling-in
Silica gel in the amount necessary for
commissioning of the autotransformer : Yes
124. Fire-fighting system to be used in cases of inner
damages (SERGI France) : no
125. Automatics cabinet for the cooling system : Yes
Device for monitoring the condition of 750,
330 kV bushings of autotransformer : Yes
126. Power and control cables with copper cores with
retardant insulation to be used for connection of
the current transformers, control and signaling
devices; screened cables with retardant insulation
for connection of the gauges with analogous signal
of Pt100, 4…20 mА… type; which are to be laid
within the autotransformer range in stainless
steel hoses of diameters,mm2:
- From current transformers : 2.5
- From monitoring devices : 1.5
Structures on the autotransformer tank for laying
power and control cables : Yes
A set of spare parts with a mandatory supply of a
backup safety membrane of the OLTC contactor : Yes
127. Supply technical support (condition and
completeness accepting together with manufacturer
and Supplier, installation supervision)
: Yes, in the absence of force majeure
circumstances on the territory of Ukraine (in
case safety level is less or equal 2 by Ministry
of Foreign Affairs in Japan)
Documentation (in Ukrainian) to be submitted
: English; all documents
Ukrainian; Technical Specification, Installation
& O&M manual, Factory Acceptance Tests Reports
(Certificates)
128. Complete Set Data Sheet : Yes
129. Quality Certificate : Yes
130. Origin Certificate : Yes
131. Certificates for autotransformer and completing
parts (products) of the system : Yes
Instructions for transportation, unloading,
storage, installation and commissioning of the
autotransformer : Yes
Dimensional and installation drawings of the AT,
control cabinet diagrams (electrical principle
diagram, diagram of electrical connections,
installation of control cables), diagrams of the
drive and OLTC regulator : Yes
132. Technical Description and Operation Manuals or
Operation Guidelines (which include the
documentation for planned repair) for the
autotransformer, completing parts and systems
: Yes
133. Control Diagrams of the Cooling Systems and OLTC
: Yes
Test programs and methods of control
: Yes
134. Transfer-Acceptance Tests Protocols (Certificates)
: Yes
Shall submit Factory Acceptance Test Reports.
Further Type Test as per IEC Standards excluding
Short Circuit Test shall conducted on 1st
Transformer. Calculations towards Short Circuit
shall be submitted during detailed engineering.
135. Maximum height of the equipment for transportation : 4.5m
*- The parameters are to be determined by the
transformer manufacturer
Total price of the Equipment
Grand Total