## Slide 1: Water Supply System: from Water Sources to Distribution
No. T2 Ver. 1
Amagasaki Water Treatment Plant,
Hanshin Water Supply Authority

## Slide 2: Contents
      Introduction
      Water Sources and Treatment Systems
      Development of Surface Water
      Treatment Processes and Water Quality Control
      Groundwater Use and Prevention of Land Subsidence
      Distribution Systems
      Engineering Design and Master Plans
      Lessons Learned

## Slide 3: 1. Introduction
Securement of water sources
Water treatment facilities suitable for different water sources
Water transmission and distribution system
Engineering Design
Annual water supply volume in Japan
JWWA, Water Supply Services Overview, 6th edition (2015) p.21
Development of water supply systems raised the amount of drinking water supply in Japan sharply since the 1950s.
What is the water supply system?

## Slide 4: 1. Introduction
Q1. How did Japanese water utilities choose water sources and maintain facilities for stable and economical safe water supply?
Q2. How did they develop water sources to meet increasing demand? How did they manage the conflicts with other water use? How do they share the cost with other stakeholders in water resource development?
Q3. How water source developed for water supply in wide areas? How the Bulk Water Supply is managed?
Q4. How did Japan control pollution of water sources?
Q5. How did Japan overcome land subsidence?
Q6. How did Japanese utilities develop water distribution pipelines? What are characteristics of them?
Q7. Why does Japan emphasize planed facility constructions? How do Japanese water utilities steadily develop water supply facilities in required level? How master plans are made and utilized?
Frequently asked questions from participants of the water supply training courses

## Slide 5: 2. Water Sources and Treatment System
Water source from mountain stream
Meteorological water
(rain water)
Spring water, stream water, groundwater
Surface water from dam reservoirs and rivers
Plentiful but contaminated
River water has been used in response to increased water demand.
Need to prevent microbial contamination.
Quantity
It is better to select clean and safe water sources without microbial contamination.

## Slide 6: 3. Development of Surface Water
In Japan, water rights has been established pursuant to state law for the orderly allocation of water and to manage conflicts among stakeholders, with due considerations to customary water rights.
The Shiroyama Dam and Lake Tsukui
  (1) Water Rights
1896 Former River Act included the concept of water rights system.
1961 Current water rights system was established.
Multi-purpose dam for cost efficiency
Coordination of the interests of stakeholders
Watershed conservation

## Slide 7: 3. Development of Surface Water
Ogouchi Dam
1951 Comprehensive River Development Project started.
1961 Act on Advancement of Water Resources Development enacted.
For financial efficiency, multipurpose dams are constructed by sharing the burden with other water users and river administrators.
  (2) Comprehensive River Development
Water saving and leakage reduction were proactively promoted in order to reduce the cost of water resources development.
In Japan, in order to meet increasing water demand, water sources were developed mainly by multipurpose dams planned under the Comprehensive River Development Projects, which covered and coordinated water use, flood control and environmental conservation.

## Slide 8: 3. Development of Surface Water
Yoshino River
Sameura Dam site
Kagawa Canal
Tokushima
Kochi
  Example: Coordination of Water Use through Comprehensive Development: Kagawa Canal in Shikoku Region
National government steps in by:
Bringing together key stakeholders in planning how to develop the entire Shikoku Region
Making a special act for the plan
Transparent and fair sharing of hydrological data set by the initiative of the national government
Discussing comprehensive river basin management, covering not only water use by Kagawa Pref., but also flood control needs of Tokushima Pref.
Providing compensation for negatively-affected Kochi Pref., where dam site is located, from the beneficiary, Kagawa Pref., such as subsidy for forestry
New user: Kagawa Pref.
Dam site: Kochi Pref.
Flood: Tokushima Pref.
Historic user:
Tokushima Pref., Ehime Pref.
Shikoku Region
Ehime
Kagawa
Conflict management

## Slide 9: 3. Development of Surface Water
Source: Bureau of Waterworks Tokyo Metropolitan Government
https://www.waterworks.metro.tokyo.jp/kids/study/images/study_13-14-15-16.pdf
1957 Commissioning of the Ogouchi Dam in Tokyo
1964 Serious drought during Tokyo Olympics
1965 Commissioning of the raw water transmission pipe connecting the Tone River (outside of Tokyo) and the Tama River (in Tokyo)
1965 Commissioning of the Musashi Channel to bring more water from other prefectures to Tokyo
  Example: Water source development by the Tokyo Metropolitan Government Bureau of Waterworks
Musashi Channel
Tama River
Arakawa River
Tone River
Ogouchi Dam
Transmission pipe
Water resource and Tokyo area
Tokyo

## Slide 10
Wastewater Treatment Plant
  (3) Watershed Conservation
In Japan, steady and long-term efforts were made not only for the purpose of water supply, but also for the improvement of water quality in the entire watersheds.
River cleaning campaign
Effluent regulation
Wastewater treatment plants
Conservation of forests in water source areas
3. Development of Surface Water

## Slide 11: 3. Development of Surface Water
Intake of water in the downstream of rivers can aggravate salt water intrusion. Japan dealt with this issue by installing estuary barrages.
Simple estuary barrage in Okayama city
  (4) Salt Water Intrusion
River flow
River water
Sea water

## Slide 12: 3. Development of Surface Water
  (5) Bulk Water Supply
Bulk Water Supply
Note: Bulk Water Supply in Japan are operated by public institutions, and different from the private bulk water supplies often seen in developing countries.
Securing of water sources
Reduction of investment costs
Large-scale water sources for the project in a wide region

## Slide 13: 3. Development of Surface Water
An example of water supply integration
(Iwate Chubu Water Supply Authority)
P
P
R
R
Kitakami City
Hanamaki City
Shiwa Town
Iwate Tyubu Water Treatment Plant
Main WTP
  (5) Bulk Water Supply
P
P
Small WTP
P
P
R
R
Small WTP
Small WTP
R
P
P
Main WTP
P
Small WTP
Main water treatment plant is connected to other small water treatment plant
Small WTP
Stable water supply.

## Slide 14: 4. Treatment Process
The effectiveness of chlorination was recognized as countermeasure against deteriorated public health in Japan after World War II .
Advantages
Very effective against waterborne diseases
Reliable disinfection
Easy to operate
Simple injection device
Low cost
  (1)Chlorination
Disadvantages
Toxicity
Generation of disinfection by-products
Corrosion of equipment
Over-reliance on chlorination may lead to neglect of water purification technology
Chlorination has prevented waterborne diseases, which were caused by contamination of water sources.
Chlorination is the most effective disinfection method for the drinking water supply.

## Slide 15: 4. Treatment Process
  Water Treatment Using Chlorine
Pre-chlorination to remove algae and ammonia(a)
Generation of chloramines (a)
Break point chlorination
High injection rate to
reduce the chloramine
generate free chlorine (c)
Destruction of chloramines (b)
Oxidation of manganese by chlorine
Rapid and certain removal by filtration of manganese sand, which has manganese dioxide coating.
Ammonia Removal （Break point chlorination）
Manganese Removal
Break point
Concentration of
residual chlorine
Pre-chlorination
Destruction of chloramines
Generation of chloramines
(a)
(ｂ)
(ｃ)
Chlorine dosing rate
Source: Ministry of the Environment,
Government of Japan,
http://www.env.go.jp/hourei/05/000188.html
Generation of free chlorine

## Slide 16: 4. Treatment Process
  The Standards of Chloride Concentration
After the World War II, GHQ prescribed the chlorine dosing rate based on their experiences in a developing country.
It was too high in Japan, where hygiene conditions were rather well-maintained.
After independence, the Japanese government reduced the chlorine dosing rate.
Residual chlorine at tap; 2.0 mg/l
Free residual chlorine at tap; 0.1 mg/l
Combined residual chlorine ; 0.4 mg/l
Bringing in the precedents without considering local situation

## Slide 17: 4. Treatment Process
Water treatment facilities play a central role in water supply systems and its performance has a direct impact on the quality of the water supplied.
  (2) Selection of Treatment Process
Disinfection
Slow sand filtration
Spring water, stream water, pure shallow groundwater
Surface water with much turbidity
Rapid sand filtration
Disinfection
Disinfection
Good water quality
Abundant water volume
Surface water with less turbidity

## Slide 18: 4. Treatment Process
Slow sand filtration is suitable for relatively clean raw water.
It provides biological treatment when water passes through a gelatinous layer (or biofilm) which consists of algae and bacteria, etc.
  (3) Slow Sand Filtration
Yanagasaki water treatment plant, Otsu City Public Enterprise Bureau
Source: Otsu city Public Enterprise Bureau, Main water supply facilities http://www.city.otsu.lg.jp/kigyo/about/water/1454032216393.html
Advantages
Simple facilities
Less chemicals and electricity
Removal of odor
Gravity settling in sedimentation tank
sand filtration with filtration velocity 4 – 5 m/day
(Japanese standards)
chlorination

## Slide 19: 4. Treatment Process
In the early days of construction of water supply systems in Japan, slow sand filtration was selected for treatment of small volumes of relatively clean raw water. In response to the increasing demand, coagulation, sedimentation, and rapid sand filtration became the mainstream treatment technology.
  (4) Rapid Sand Filtration
The first plant using rapid sand filtration in Japan(Keage WTP, Kyoto City)
Advantages of RS filtration
Adjusts to changes in turbidity
Less space for facility
Removal of highly concentrated ammonia
Economic growth caused a huge water demand
Intake points were moved downstream to get larger water volumes
High in contaminants and high turbidity

## Slide 20: 4. Treatment Process
?
Smaller footprint than slow sand filters, making it possible to built in a small plots.
Increased levels of ammonia in source waters due to contamination beyond the ability of slow sand filtration.
It may be only a trend; it was the most advanced technology at that time.
  The Background of Widespread Application of Rapid Filtration
Why rapid filtration was selected in Japan?
Disruption of river bed caused by digging for construction materials.

## Slide 21: 4. Treatment Process
Exacerbating pollution of source waters has reached to the levels that made it difficult to treat source waters by conventional water treatment processes designed for the removal of turbidity and disinfection. Japan has carried out a series of studies for the combination of various water treatment technologies to develop advanced water treatment technologies.
  (5) Advanced Water Treatment
Activated carbon adsorption =Biological reactor
Ozonation =Oxidize organic matter
Ozone contact basin
Tokyo Metropolitan Government Bureau of Waterworks：https://www.waterworks.metro.tokyo.jp/suigen/topic/13.html
Removal of odor and organic substances improves drinking water quality.

## Slide 22: 4. Treatment Process
Advantages of membrane filtration technology requires less land areas, low maintenance and minimal manpower because it is easy to control automatically.
The use of membrane filtration is expected to increase around the world in the future.
  (6) Membrane Filtration
1994-1996 MAC 21 research project; Industry-government-academia collaboration
Membrane filtration technology continues to be developed.
Membrane filtration facilities, Water supply system for Kuroda area in Kyoto city, Waterworks Bureau, City of Kyoto
http://www.city.kyoto.lg.jp/suido/page/0000160981.html

## Slide 23: 4. Treatment Process
  (7) Water Reuse
Sewage treatment plant
Discharge to the river
Drinking water
Intake and water treatment plant
Indirect water reuse
Grey water
Water reuse can be an option even in developing countries, when water resources become too scarce or degraded to be handled with ordinary water supply systems.
In Japan, reused water is not used directly for potable use. It is used mainly for industrial process water and toilet flushing in regions where the use of groundwater is strictly regulated (ex. Tokyo) or in regions where water resources frequently run short.

## Slide 24: 4. Treatment Process
  (8) Wastes from Treatment Plants
The sludge from the sedimentation system is sent to gravity thickener
and condensed by gravity thickener.
The filter backwash water is sent to filter backwash clarifier then it is sent to gravity thickener.
The dewatered sludge is often disposed but it is sometimes utilized for materials for cements, playgrounds and agricultural compost etc.
Drinking water
Filter backwash clarifier
Gravity thickener
Dewatering process
Rapid sand
filters
Flash mixing chamber
Sedimentation basin
Flocculation basin
Receiving well

## Slide 25: 5. Groundwater Use and Prevention of Land Subsidence
In general, groundwater is clear and suitable as a drinking water source. But in some cases, it requires treatment to meet water quality guidelines.
Groundwater source
（Takizawa Village, Iwate Prefecture）
Check water quality carefully because some groundwater is not good for drinking water.
Maintain and monitor the well regularly.
Contaminated by
Fe, Mg, As…or E. Coli.
  (1) Groundwater Withdrawal

## Slide 26: 5. Groundwater Use and Prevention of Land Subsidence
Japan experienced serious land subsidence in some regions, but has brought it under control by introducing strict regulations for use by industries and large buildings, and supplying alternative sources such as surface water and reclaimed wastewater.
Preventing overuse of groundwater to avoid negative effect of land subsidence
  (2) Land Subsidence
Monitoring of the levels of ground and groundwater tables
Introduce regulations for pumping groundwater to restrict water withdrawal
Monitor groundwater levels, land subsidence and groundwater withdrawal regularly
Provide other water sources instead of groundwater

## Slide 27: 5. Groundwater Use and Prevention of Land Subsidence
Today Japan has almost stopped land subsidence.
1950s Land subsidence became recognized as a serious social problem causing flooding and lifting of buildings.
  The Background of Land Subsidence in Japan
Various countermeasures
Total Subsidence (cm)
Tokyo
Lifting phenomena at pumping facility
Osaka
1930s-40s The cause of land subsidence was found to be excessive groundwater pumping.
No countermeasures, economic recovery was priority
Other Cities

## Slide 28: 6. Distribution Systems
The investment in distribution infrastructure such as service reservoirs, pump stations and pipelines is very costly and it accounts for 2/3 of the total capital cost of all the water supply facilities. Therefore, good planning of the distribution system based on the long-term perspective is very important.
Elevated tank,
Hachinohe Region Water Supply Authority
For good planning,
Construct service reservoirs in high places
Use elevated tanks when there is no suitable high place
Plan the capacity of service reservoirs and distribution network based on the long-term water demand projection
Understand pump technology and water hammer pressure to prevent critical damages to the system
  (1) Distribution Systems

## Slide 29: 6. Distribution Systems
  (2) Pipeline Configuration
The planning policy for distribution pipelines has been changing gradually in Japan, from simple distribution to more sophisticated control of water distribution.
1st stage: Tree (dendritic) system for simple distribution
2nd stage: Network system to minimize the negative impact of accidents and ensure operational flexibility
3rd stage: Block system for
(1) optimizing water pressure
(2) clear picture of water supply operation
(3) identification of accidental damage and provision of backup water supply
Tree system
Network system
Monitoring and control point to find leakage
Block system

## Slide 30: 7. Engineering Design and Master Plans
The most important concept for water supply is to secure the safe supply of water through well-designed water facilities. The design standards to define the function and capacity of water facilities are specified in the Water Supply Act.
Update the Design Criteria on a regular basis
  (1) Importance of Facility Standards
It has been complementing the design standards of the Water Supply Act.
Share know-how among senior engineers of major water utilities
Need to acquire design methods and accumulate technical knowledge
Coordinated by
Japan Water Works Association
Build up the Design Criteria for Water Supply Facilities

## Slide 31: 7. Engineering Design and Master Plans
  (2)Updating the Design Concepts
The Great Hanshin/Awaji Earthquake 1995
The Great East Japan Earthquake 2011
Damage was reduced.
Improvement in preparedness
The design concepts for water supply facilities need to be improved, reflecting the situations of each country. For example, since Japan is an earthquake prone country, the design of water supply facilities has been improved gradually based on lessons learned from the damage of past earthquakes.
Anti-seismic pipeline for distribution main
Efforts to secure emergency water supply
Manuals for Emergency Response in Earthquakes
Seismic Design and Construction Guidelines for Water Supply Facilities

## Slide 32: 7. Engineering Design and Master Plans
Water facilities
Water supply systems require large amounts of funding for construction, and therefore, must be expanded step by step, based on medium to long-term master plans including business plans with sound financial policy.
  (3) Step by Step Expansion
Pipe network
Finance
Water resource
Water facilities
Primary master plan
Organization
Pipe network
Finance
Water resource
Organization
Updated master plan
Adjust master plan step by step according to actual income and finance
City A
10 -year plan
Construction first year
Construction 5 years
Construction 10 years
Land acquisition
Land acquisition

## Slide 33: 7. Engineering Design and Master Plans
As Japan has shifted from the expansion stage to the maintenance stage, Approval(License) is now supplemented by the following plans and systems:
Application for License
Used for screening to obtain subsidy
  (4) System to Validate Proper Operation and Management
A master plan
Prepared with technical assistance by prefectural governments and health centers.
・Demand prediction
・Facility plan
・Financial plan
（Tariff setting）
Approval (License), stipulated in the Water Supply Act, requires a master plan. It was effective in the early stage of expansion when water utilities were not yet technically sophisticated.
Waterworks Vision
Water Safety Plan
Annual business plan and budget to be approved by local councils
Asset Management

## Slide 34: 8. Lessons Learned (1)
  (Selection of Water Source) It is ideal if pristine water sources can be used for drinking water supply. This is especially important for small- and medium-scale utilities that are in short of human resources and technical capabilities.
  (Surface Water Development) The water rights system and Comprehensive River Development were effective for developing water resources. It requires cooperation of stakeholders, negotiations and sometimes conflict management. Dam construction is expensive, so that municipalities needed to get together and work with other users and river authorities on multipurpose dam construction. They also organized to secure Bulk Water Supply.
  (Chlorination) Chlorination contributed a lot to the supply of safe tap water. However, it has some disadvantages including; production of disinfection by-products, formation and corrosion of equipment.
  (Rapid Sand Filtration) The coagulation, flocculation, sedimentation and rapid sand filtration process is often used to treat highly polluted raw water. The choice depends on quality of the raw water and water demand. Many utilities use this method to treat large volume of polluted water especially in urban area, which usually located at downstream.

## Slide 35: 8. Lessons Learned (2)
  (Dealing with Source Water Deterioration) Japan developed technologies and new approaches to deal with challenges of water source pollution and drought. These include advanced water treatment, membrane filtration and wastewater reuse. Although new technology development requires larger investment, it can produce high quality waters to win the public support for the water supply.
  (Prevention of Land Subsidence) Japan faced serious land subsidence due to over-pumping of groundwater in some regions. This problem is under control by strictly regulating groundwater abstraction, providing alternative water sources and monitoring ground levels and groundwater levels.
  (Transmission and Distribution Systems) The investment for transmission and distribution systems accounts for two thirds of the total investment cost of the water supply system, so that it is important to plan and construct distribution reservoir, pumps and pipelines efficiently based on the long-term plans. Japan has taken advantage of its hilly terrain to build gravity flow systems to save money and energy for easy control of water distribution.

## Slide 36: 8. Lessons Learned (3)
  (Block Distribution Systems) Distribution pipelines have evolved from dendritic systems, to network and block distribution systems as cities expand. The advanced designs provide better control of water distribution and minimize supply disruptions.
  (Master Plan) Japan expanded its water supply systems by well-planned and stepwise expansion to keep pace with population growth and water demand. This approach is effective for sound financial management of the utilities. Formulation of a master plan, which includes long-term projection of demographic and social changes is effective in developing water supply system and expanding water supply coverage.
  (Approval(License) System) The Water Supply Act stipulates the requirements for Approval(License), facility standards and qualification of technical administrators. These set the high standard for water supply quality and sound business management. The national government is encouraging the preparation of Water Vision and Water Safety Plan to ensure technical stability of utilities. Preparation of annual business plan, which includes budget plan based on the Local Public Enterprise Act, and the approval by the local assembly ensures sound business management.